Operating and Maintenance Manual

and Building Log Book for the

Mechanical Services Installation at

General Office Building

Reception Refurbishment

A N Other Contractors Ltd

123 High Road

London

E1 2AB

Tel: 020 7123 1234

Fax: 020 7123 5678

Volume One of One

SECTION

VOLUME ONE

ONE

TWO

THREE

FOUR

FIVE

SIX

SEVEN

EIGHT

NINE

TEN

ELEVEN

TWELVE

CONTENTS

DESCRIPTION

-

-

-

-

-

-

-

-

-

-

-

-

General Description of Installation

Plant Data Schedules

Emergency Procedures and First Aid

Health and Safety Information

Operating Procedures

Maintenance Schedules

Maintenance Instructions and Log Books

Fault Tracing Charts

Manufacturers' Literature

Test Certificates and Commissioning Data

Specialist Services Documentation

Record Drawings

SECTION ONE

GENERAL DESCRIPTION OF INSTALLATION

SECTION ONE

INDEX

ITEM

1.1

1.1.1

1.1.2

1.1.3

1.1.4

1.1.5

1.1.6

1.1.7

1.1.8

1.1.9

1.1.10

1.1.11

-

-

-

-

-

-

-

-

-

-

-

-

General Description of Installation

DESCRIPTION

PRELIMINARY ITEMS

Introduction

Document Revisions

Purpose of Each Section

Schedule of Abbreviations

Schedule of Services Identification

Specific Health and Safety Issues

Incoming Services Location

Emergency Telephone Numbers

Schedule of Project Team Members

Brief Description of Installation

Design Criteria

HEATING AND COOLING SYSTEMS

Air Conditioning System

MISCELLANEOUS SYSTEMS

Specialist Services

1.2

1.2.1

-

-

1.3

1.3.1

-

-

General Office Building, Reception Refurbishment

Section 1, Page 2

SECTION ONE

Title: Introduction

Category: Preliminary Items

General Description of Installation

Item: 1.1.1

Page: 1 of 1

The purpose of this operating and maintenance manual and building log book is to offer the personnel

concerned with the operation and maintenance of the services within the building,  assistance in the

performance  of  their  duties.  It  is  intended  that  this  manual  will  be  used  to  assist  skilled  engineers,

experienced in the operation and maintenance of building services, to provide them with a comprehensive

working knowledge of the various systems installed within the project.

Although  the  manual  functions  as  a  complete  entity,  each  section  is  self  contained  and  provides

information on differing aspects of the installation. Familiarisation with all sections prior to formulating

an operating and maintenance regime will prepare the building maintenance personnel for the occasions

when a particular problem occurs.

The  information,  procedures  and  instructions  contained  herein  are  those  appertaining  at  the  time  of

preparation and the date of issue. Changes arising in building usage, legislation, etc, will necessitate

revisions  to  be  made  in  order  to  retain  the  manual's  validity  and  usefulness.  Any  alterations  to  this

document (addition, revision or omission) should be recorded on the following page.

The information within this manual will allow maintenance to be carried out safely and reliably, as well

as  providing  important  data  upon  which  calculations  may  be  made  for  design  of  alterations  and/or

additions, should the need arise. It should be noted that this manual is not intended to supersede or conflict

with any standard maintenance/inspection routines already in use.

This manual has been based on the content suggested by the Building Services Research and Information

Association in their application guide AG 1/87.1 (Operating and Maintenance Manuals for Building

Services Installations). Where issued electronically the same organisation's guide BG 2/2004 (Computer

BasedOperatingandMaintenance Manuals)has been utilised(theirsuggested"PDFBasedSystem").This

manual has also been compiled to cater for other industry legislation requirements such as Health and

Safety Executive (CDM) and the Building Regulations (Part L2) et al.

Practical Completion:

Handover:

Defects Liability Period:

Author:

June 2007

June 2007

12 Months

Manual Version:

Date of Final Issue:

Author's Reference:

5.01.04

June 2007

xxxx

Office-Scope, 43 Leicester Road, Wanstead, London, E11 2DW

Tel: 020 8536 4060, Fax: 020 8536 4061

E-mail: <recipient>@office-scope.co.uk, Website: www.office-scope.co.uk

This manual is also available as a fully interactive electronic document suitable for direct use on a computer

For further details or to obtain a quotation, please contact the author with your requirements quoting the above reference number.

General Office Building, Reception Refurbishment

Section 1, Page 3

SECTION ONE

Title: Document Revisions

Category: Preliminary Items

General Description of Installation

Item: 1.1.2

Page: 1 of 1

Initial Production

Stage of Development (all dates refer to author)

Draft Copy Production Commenced

Draft Copy Issued

Comments Received, Information/Clarification Sought

Information/Clarification Received, Final Copy Production Commenced

Final Copy Issued

Date

21/5/2007

23/5/2007

25/6/2007

27/6/2007

28/6/2007

Date

Subsequent Revision History

Description of Revisions

General Office Building, Reception Refurbishment

Section 1, Page 4

SECTION ONE

Title: Purpose of Each Section

Category: Preliminary Items

General Description of Installation

Item: 1.1.3

Page: 1 of 1

Section One - General Description of Installation - This section contains a general description of each system,

together with other introductory information. The descriptions are intended to be read in conjunction with the Record

Drawings to aid the maintenance personnel in familiarising themselves within the installation, prior to formulating

an operating and maintenance programme.

Section Two - Plant Data Schedules - This section contains the technical data for each item of equipment extracted

from the manufacturers' literature and other sources to assist with the maintenance and possible replacement of faulty

items of equipment. Recommended stocked spares list, lubricants, special tools and equipment are also included.

Section  Three  -  Emergency  Procedures  and  First  Aid  -  This  section  contains  the  procedures  that  should  be

followed in the event of an emergency, together with the emergency call-out telephone numbers for the local utility

companies and basic first aid instructions.

Section Four - Health and Safety Information - This section contains check lists and safety procedures that should

be followed to ensure that the operation and maintenance of the installation is undertaken in a safe manner.

Section Five - Operating Procedures - This section contains all necessary operational procedures for the systems.

It  is  intended  that  the  procedures  are  read  in  conjunction  with  the  manufacturers'  literature  so  that  operational

procedures are extended beyond each item of equipment and cover the full system.

Section  Six  -  Maintenance  Schedules  -  This  section  contains  schedules  of  maintenance  tasks  for  each  item  of

equipment. It is intended for use in the formulation of a Planned Preventative Maintenance regime. The schedules

are intended to be read in conjunction with the manufacturers' literature for detailed maintenance instructions.

Section  Seven  -  Maintenance  Instructions  and  Log  Books  -  This  section  contains  various  instructions  and

procedures  necessary  when  implementing  an  operating  and  maintenance  regime,  including  risk  assessments,

handling/disposal instructions, decontamination procedures and recommendations on the use and keeping of energy

usage and maintenance log books, together with sample log book documentation.

Section Eight - Fault Tracing Charts - This section contains charts to assist with the location of faults that occur

with  systems.  Once  the  appropriate  faulty  item of  equipment  has  been  located,  the  fault  tracing  chart  within  the

manufacturers' literature should be consulted to remedy the problem.

Section Nine - Manufacturers' Literature - This section contains the manufacturers' literature for each item of

equipment. This information should be used in conjunction with various sections as described above.

Section  Ten  -  Test  Certificates  and  Commissioning  Data  -  This  section  contains  the  test  certificates  and

commissioning data that should be consulted when carrying out maintenance tasks, or fault tracing procedures, to

ensure the correct and efficient operation of each system.

Section Eleven - Specialist Services Documentation - This section contains the small independent manuals from

the specialist sub-contractors which contain all necessary operating and maintenance information.

Section Twelve - Record Drawings - This section contains a copy of each of the Record Drawings which should

be read in conjunction with the general descriptions and are intended to assist the maintenance personnel with the

familiarisation of the installation.

General Office Building, Reception Refurbishment

Section 1, Page 5

SECTION ONE

Title: Schedule of Abbreviations

Category: Preliminary Items

Type

General Description of Installation

Item: 1.1.4

Page: 1 of 2

Equipment

Abbreviation

AHU

FCU

SD

MD

SG

LSD

TG

RC

DRV

NRV

DC

GC

Meaning

Air Handling Unit

Fan Coil Unit

Smoke Damper

Motorised Damper

Supply Grille

Linear Slot Diffuser

Transfer Grille

Roof Cowl

Double Regulating

Valve

Non-Return Valve

Drain Cock

Gas Cock

Abbreviation

EF

VAV

FD

VCD

SD

EG

WL

IV

CS

STR

DX

SC

DCV

Double Check Valve

PRV

SV

Safety Valve

BV

Meaning

Extract Fan

Variable Air Volume

Fire Damper

Volume Control

Damper

Supply Diffuser

Extract Grille

Weather Louvre

Isolating Valve

Commissioning Set

Strainer

Direct Expansion

Stop Cock

Pressure Relief Valve

or Pressure Reducing

Valve

Ball Valve

General Office Building, Reception Refurbishment

Section 1, Page 6

SECTION ONE

Title: Schedule of Abbreviations

Category: Preliminary Items

Type

General Description of Installation

Item: 1.1.4

Page: 2 of 2

Systems

Abbreviation

LTHW

MTHW

CHW

VRV

MWS

CWDS

HWS

BMS

F&R

CF

OV

F&E

Meaning

Low Temperature Hot Water

Medium Temperature Hot Water

Chilled Water

Variable Refrigerant Volume

Mains Water Service

Cold Water Down Service

Hot Water Service

Building Management System

Flow and Return

Cold Feed

Open Vent

Feed and Expansion

Type

Units

Abbreviation

oC

wb

W

mm

kg

kPa

m  3/s

kg/h

rpm

V

Meaning

Degree Celsius

wet bulb

Watts

milli-metres

kilo grammes

kilo Pascals

cubic metres per

second

kilo grammes per hour

revolutions per minute

Volts, Voltage

Abbreviation

db

% RH

kW

m

Pa

m/s

kg/s

l/s

Hz

A

Meaning

dry bulb

Relative Humidity

kilo Watts

metres

Pascals

metres per second

kilo grammes per

second

litres per second

Hertz

Amps

General Office Building, Reception Refurbishment

Section 1, Page 7

SECTION ONE

Title: Schedule of Services Identification

Category: Preliminary Items

General Description of Installation

Item: 1.1.5

Page: 1 of 1

The services installed on this project have been identified by coloured bands in accordance with BS 1710

(1984). The following table illustrates this colour code:-

Service

Coloured Strips

Mains Water

Natural Gas

Steam

Low Temperature Hot Water

Medium Temperature Hot

Water

Chilled Water

Refrigerant R22

Refrigerants

R134a/R407c/R410a

Cold Water Down Service

Hot Water Service

Drainage

Compressed Air

Basic Colour

PIPEWORK

Green

Yellow Ochre

Auxiliary Blue

Yellow

Silver Grey

Blue/Crimson/Blue

Crimson/Blue/Crimson

Green

Green

Green

Yellow Ochre

Yellow Ochre

White/Emerald Green/White

Sea-Green

Emerald Green

Green

Green

White/Blue/White

White/Crimson/White

Black

Light Blue

DUCTWORK

Green Triangle

Red/Blue Triangle

Yellow Triangle

Red Triangle

Blue Triangle

Grey Triangle

Brown Triangle

Yellow/Black Triangle

Fresh Air

Conditioned Air

Warm Air

Hot Supply Air

Cold Supply Air

Exhaust Air

Foul Air

Contaminated/Hazardous Air

General Office Building, Reception Refurbishment

Section 1, Page 8

SECTION ONE

Title: Specific Health and Safety Issues

Category: Preliminary Items

General Description of Installation

Item: 1.1.6

Page: 1 of 1

The following information is a summary of the key Health and Safety issues regarding the project covered

by this document. It is imperative that the main Health and Safety section later within this document and

the main project Health and Safety File are fully consulted.

Residual Risks

The project has been designed to avoid there being any residual risks.

Special Access Requirements

The project has been designed to avoid the need for any special access requirements.

Special Maintenance Considerations

The project has been designed to avoid the need for any special maintenance considerations.

General Office Building, Reception Refurbishment

Section 1, Page 9

SECTION ONE

Title: Incoming Services Location

Category: Preliminary Items

The main incoming services are located in the following locations:-

Gas

Water

Electricity

-

-

-

General Description of Installation

Item: 1.1.7

Page: 1 of 1

Not applicable to the contract covered by this manual

Not applicable to the contract covered by this manual

Refer to electrical manual.

General Office Building, Reception Refurbishment

Section 1, Page 10

SECTION ONE

Title: Emergency Telephone Numbers

Category: Preliminary Items

The following telephone numbers are for emergency use only:-

Gas

Water and Sewage

Electricity

Police

Fire Brigade

Ambulance

-

-

-

Transco

Thames Water

EDF Energy (London)

General Description of Installation

Item: 1.1.8

Page: 1 of 1

-

-

-

0800 111999

0800 714614

0800 028 0247

-

Emergency Services Operator

-

999

General Office Building, Reception Refurbishment

Section 1, Page 11

SECTION ONE

Title: Schedule of Project Team Members

Category: Preliminary Items

Project Team Role

General Description of Installation

Item: 1.1.9

Page: 1 of 2

Company

A N Other Client Ltd

123 High Road

London

E1 2AB

Tel: 020 7123 1234

Fax: 020 7123 5678

A N Other Employers Agent Ltd

123 High Road

London

E1 2AB

Tel: 020 7123 1234

Fax: 020 7123 5678

A N Other Architect Ltd

123 High Road

London

E1 2AB

Tel: 020 7123 1234

Fax: 020 7123 5678

A N Other Planning Supervisor Ltd

123 High Road

London

E1 2AB

Tel: 020 7123 1234

Fax: 020 7123 5678

A N Other Consultant Ltd

123 High Road

London

E1 2AB

Tel: 020 7123 1234

Fax: 020 7123 5678

Client

Employers Agent

Architect, Project Manager and

Contract Administrator

Planning Supervisor

Property Consultant

General Office Building, Reception Refurbishment

Section 1, Page 12

SECTION ONE

Title: Schedule of Project Team Members

Category: Preliminary Items

Project Team Role

General Description of Installation

Item: 1.1.9

Page: 2 of 2

Consultant Engineer

Main Contractor

Services Contractor

Company

A N Other Consultant Ltd

123 High Road

London

E1 2AB

Tel: 020 7123 1234

Fax: 020 7123 5678

A N Other Builder Ltd

123 High Road

London

E1 2AB

Tel: 020 7123 1234

Fax: 020 7123 5678

A N Other Contractor Ltd

123 High Road

London

E1 2AB

Tel: 020 7123 1234

Fax: 020 7123 5678

General Office Building, Reception Refurbishment

Section 1, Page 13

SECTION ONE

Title: Brief Description of Installation

Category: Preliminary Items

General Description of Installation

Item: 1.1.10

Page: 1 of 1

The  following  is  an  outline  description  of  the  services  installed  under  the  contract  covered  by  this

document; for a full description of each system reference should be made to the following pages.

Heating and Cooling Systems

a)

A direct expansion heat pump split air conditioning system consisting of a void mounted ducted

internal unit which is connected to an air cooled condensing unit located on the roof.

Specialist Services

The contract covered by this document also encompassed various specialist services/systems as detailed

below, whichweresupplied,installed,testedandcommissionedby thespecialistsub-contractorindicated.

For full information relating to each system reference should be made to the self-contained specialist

manuals located within Section Eleven.

Mechanical Services Control System      -            A N Other Controls Company Ltd

General Office Building, Reception Refurbishment

Section 1, Page 14

SECTION ONE

Title: Design Criteria

Category: Preliminary Items

The following criteria were used during the design of the installation:-

External Conditions

Summer Temperature

Winter Temperature

Internal Conditions

Summer Temperature

Winter Temperature

-

-

General Description of Installation

Item: 1.1.11

Page: 1 of 1

31.0 oC db, 21.0 oC wb

-4.0  oC saturated

-

-

22.0 C  +/  2.0 oC, No Humidity Control

21.0 C  +/  2.0 oC, No Humidity Control

-

o

-

o

General Office Building, Reception Refurbishment

Section 1, Page 15

SECTION ONE

Title: Air Conditioning System

Category: Heating and Cooling Systems

General Description of Installation

Item: 1.2.1

Page: 1 of 1

A direct expansion heat pump split air conditioning system has been installed to provide both heating and

cooling to the Reception. The internal unit is void mounted above the reception desk and incorporates a

washable panel filter, a direct expansion heating/cooling coil and a direct driven centrifugal fan unit. Air

is drawn into the unit from the false ceiling void via a shadow gap in the ceiling, heated or cooled as

required and supplied back to the space via ranges of galvanised steel spiral ductwork which serve plenum

boxes located above a shadow gap on the opposite side of the space.

Liquid and suction refrigeration pipework extends from the internal unit to run through the false ceiling

void of the ground floor on a series of galvanised steel cable tray. The pipework then enters a building

services riser shaft where it rises through the building onto the roof and connects onto an air cooled

condensingunit.Thecondensingunitincorporatesadirect driven propeller condenserfanandarefrigerant

compressor.

The internal unit is controlled under the dictates of a return air sensor located within the return air path.

Condensate from the internal unit discharges into a gravity condensate drain run within the false ceiling

void which, in turn discharges into the existing above ground drainage system.

The pipework is insulated with a closed cellular foam insulation in order to reduce heat gain to the system

and vapour sealed to prevent the formation of condensation on the pipe surface.

For the locations of the equipment and the routes of the pipework reference should be made to the Record

Drawings contained within Section Twelve.

General Office Building, Reception Refurbishment

Section 1, Page 16

SECTION ONE

Title: Specialist Services

Category: Miscellaneous Systems

General Description of Installation

Item: 1.3.1

Page: 1 of 1

The contract covered by this document also encompassed various specialist services/systems as detailed

below, whichweresupplied,installed,testedandcommissionedby thespecialistsub-contractorindicated.

For full information relating to each system reference should be made to the self-contained specialist

manuals located within Section Eleven.

Mechanical Services Control System      -            A N Other Controls Company Ltd

General Office Building, Reception Refurbishment

Section 1, Page 17

SECTION TWO

PLANT DATA SCHEDULES

SECTION TWO

INDEX

ITEM

2.1

2.1.1

2.1.2

2.1.3

2.1.4

2.1.5

-

-

-

-

-

-

Plant Data Schedules

DESCRIPTION

MISCELLANEOUS ITEMS

Directory of Manufacturers

Spare Parts Policy

Recommended Stocked Spares

Lubricants

Special Tools and Equipment

HEATING AND COOLING SYSTEMS

Air Conditioning Units

2.2

2.2.1

-

-

General Office Building, Reception Refurbishment

Section 2, Page 2

SECTION TWO

Title: Directory of Manufacturers

Category: Miscellaneous Items

Name

A N Other Controls

Company Ltd

Plant Data Schedules

Item: 2.1.1

Page: 1 of 1

Address

123 High Road

London

E1 2AB

Tel: 020 7123 1234

Fax: 020 7123 5678

Orbital One

Unit 8 & 9 Green Street

Green Road

Dartford

Kent

DA1 1QG

Tel: 01322 628080

Fax: 01322 628081

Mitsubishi Electric

Europe Ltd

Equipment Supplied

Mechanical Services Control

System

Air Conditioning Units

General Office Building, Reception Refurbishment

Section 2, Page 3

SECTION TWO

Title: Spare Parts Policy

Category: Miscellaneous Items

Plant Data Schedules

Item: 2.1.2

Page: 1 of 1

A majority of the manufacturers' literature detail a full parts list, commonly with exploded view diagrams,

however, these lists are not intended to be interpreted as spares which should be stocked, rather a list of

the part numbers should a spare need to be ordered.

The determination of what spares at what quantities should be stocked will depend upon a number of

factors, including:-

i)

ii)

iii)

iv)

v)

The degree of in house or sub-contracted maintenance.

The economic factors.

The implications of system failure to the occupiers of the premises.

The level of back-up or redundancy offered by the systems.

The lead time of spares.

In  order  to  determine  the  list  of  spares  which  should  be  stocked  the  following  questions  should  be

considered.

1)

2)

3)

What parts of the system are consumable and will require routine replacement for the safe

and efficient operation of the system. Such items include filters, drive belts, fuses and

lamps.

What systems are critical to the operation of the business, consideration should be given

to the stocking of spare motors for such systems. Particularly critical systems will usually

have a certain level of redundancy designed into the system, commonly in the form of run

and standby fans/pumps, but occasionally with 100% system backup. In such situations

the stocking of spare motors may not be necessary.

What systems are less critical but which involve extended lead times for delivery of

spares.

Once a list of which items need to be stocked has been established, consideration needs to be given to the

quantity of stock to be held. Important points include:-

a)

b)

c)

d)

The shelf life of spares, for instance drive belts generally have an expiry date.

How  often  will  it  be  necessary  to  order  new  items,  the  disposable  panel  filters  in

ventilation systems may need to be changed every two to three months.

How much storage space is available.

Is secure space available for the storage of high value items.

The following section details the minimum level of spares that are recommended to be stocked, to this

should then be added the additional items determined as a result of the consideration of the above factors.

General Office Building, Reception Refurbishment

Section 2, Page 4

SECTION TWO

Title: Recommended Stocked Spares

Category: Miscellaneous Items

Plant Data Schedules

Item: 2.1.3

Page: 1 of 1

The equipment installed on this project do not incorporate any of the following items:-

i)

ii)

iii)

Consumable parts

Parts which break easily

Parts which involve long delivery periods

therefore, there is no requirement for the stocking of spares on such grounds.

General Office Building, Reception Refurbishment

Section 2, Page 5

SECTION TWO

Title: Lubricants

Category: Miscellaneous Items

There is no plant and equipment on this project which require lubrication.

Plant Data Schedules

Item: 2.1.4

Page: 1 of 1

General Office Building, Reception Refurbishment

Section 2, Page 6

SECTION TWO

Title: Special Tools and Equipment

Category: Miscellaneous Items

Plant Data Schedules

Item: 2.1.5

Page: 1 of 1

Beyond those tools found within a "standard" tool box very few special tools or equipment are necessary

to carry out the operation and maintenance of the systems covered by this manual. Such additional items

are as follows:-

Special Tools

•            No special tools.

Equipment

•

•

•

•

•

Inclined manometer

Vane anemometer

Sling psychrometer

RPM strobe light

Electrical multi-meter

General Office Building, Reception Refurbishment

Section 2, Page 7

SECTION TWO

Title: Air Conditioning Units

Category: Heating and Cooling Systems

Internal Unit

General              -            Manufacturer

-

-

-

Model Number

Type

Duty

Plant Data Schedules

Item: 2.2.1

Page: 1 of 2

-

-

-

Cooling

Heating

-

-

Air Volume

Dimensions

-

-

-

Length

Width

Height

-

-

-

Weight

Refrigerant Type

Electrical Supply

-

-

-

-

-

-

-

-

-

-

-

Mitsubishi Electric

Europe

PEAD-RP71EA

Ceiling Concealed

6.4 kW

6.8 kW

25.0 m  3/min

1070 mm

740 mm

307 mm

44.0 kg

R410a

240 volts

1 phase

50 Hz

General Office Building, Reception Refurbishment

Section 2, Page 8

SECTION TWO

Title: Air Conditioning Units

Category: Heating and Cooling Systems

External Unit

General              -            Manufacturer

-

-

Model Number

Dimensions

Plant Data Schedules

Item: 2.2.1

Page: 2 of 2

-

-

-

-

Length

Width

Height

-

-

Weight

Refrigerant Type

-

-

Type

Charge

-

-

-

Starting Current

Full Load Current

Electrical Supply

-

-

-

-

-

-

-

-

-

-

Mitsubishi Electric

Europe

PUHZ-RP71VHA

950 mm

360 mm

943 mm

75.0 kg

R410a

3.5 kg

5.0 amps

10.17 amps

240 volts

1 phase

50 Hz

General Office Building, Reception Refurbishment

Section 2, Page 9

SECTION THREE

EMERGENCY PROCEDURES AND FIRST AID

SECTION THREE

INDEX

ITEM

3.1

3.1.1

3.1.2

3.1.3

3.1.4

-

-

-

-

-

Emergency Procedures and First Aid

DESCRIPTION

EMERGENCY PROCEDURES

Introduction

Failure of Electrical Supply

Refrigerant Leaks

Fire

FIRST AID PROCEDURES

Principles and Practice

Life Saving Measures

Emergency Situations

Dressings

Treatment for Electric Shock

Further Reading

3.2

3.2.1

3.2.2

3.2.3

3.2.4

3.2.5

3.2.6

-

-

-

-

-

-

-

General Office Building, Reception Refurbishment

Section 3, Page 2

SECTION THREE

Title: Introduction

Category: Emergency Procedures

Emergency Procedures and First Aid

Item: 3.1.1

Page: 1 of 1

The emergency procedures are intended as a guide only, each emergency situation that arises has to be

taken in the light of its degree of severity and the conditions prevailing at the time.

When an emergency situation is encountered, it is imperative that calm prevails. Measures and actions

taken when made in haste or panic, will not only in all probability be wrong, but could spread panic in

other people.

A few minutes spent in rationalising the situation and planning your campaign of actions, even in an

emergency of the utmost gravity, will save time and possibly injury in the long run.

Never take risks in an emergency, for a risk can turn a minor emergency into a major one. The safety of

personnel must always come first.

Any temporary repairs effected or arrangements made during or after an emergency must be corrected as

soon as it is practically possible.

General Office Building, Reception Refurbishment

Section 3, Page 3

SECTION THREE

Title: Failure of Electrical Supply

Category: Emergency Procedures

Emergency Procedures and First Aid

Item: 3.1.2

Page: 1 of 1

Description: This describes the general steps to take on failure of the electrical supply.

Notes:

Step

1

Action

Ascertain whether the failure is local or general.

2

If failure is local, check whether fuses have

blown, or circuit breaker has tripped.

3

If failure is general, check position of lifts (if

applicable) and hand winch to nearest lower

floor.

Notes

Check whether general lighting and

power is affected.

Replace with correct size fuse, or reset

circuit breaker as required, after

checking cause of failure and retesting

the circuit.

Isolate lift supply prior to winching.

Inform local electricity company of

failure.

Place "Lift Out of Service" notices on

all floors.

4

5

Repairs to electrical switchgear and cables

should only be undertaken by a fully qualified

electrician.

If the failure is general, isolate the supply to

items of plant until the supply is restored.

General Office Building, Reception Refurbishment

Section 3, Page 4

SECTION THREE

Title: Refrigerant Leaks

Category: Emergency Procedures

Emergency Procedures and First Aid

Item: 3.1.3

Page: 1 of 1

Description: This describes the action to take in the event of a refrigerant leak.

Notes:

1. The refrigerant that leaks out will most probably be in the form of vapour, therefore the source of

the leak will be hard to find out without proper leak detection equipment.

Step

1

Action

Shut down and electrically isolate the affected

items of plant. Check that all doors of control

panels are properly closed.

Notes

2

Evacuate all personnel from the vicinity and call

in Refrigeration Engineers.

There must not be any smoking or

flames present as they will cause the

refrigerant to break down into highly

toxic gases.

3

4

Ensure that all doors to the room are securely

shut.

It should be remembered that refrigerants are

harmful to the Ozone Layer and therefore must

be disposed of in accordance with the

requirements of the local Environmental Health

Officer.

General Office Building, Reception Refurbishment

Section 3, Page 5

SECTION THREE

Title: Fire

Category: Emergency Procedures

Emergency Procedures and First Aid

Item: 3.1.4

Page: 1 of 1

Description: This describes the action to take in the event of fire breaking out.

Notes:

1. Always inform the Fire Brigade should fire break out, and never attempt to fight it alone.

2. Never use a liquid type extinguisher to fight electrical fires.

Step

1

2

3

Action

Under most conditions occurrence of fire will be

picked up by the automatic fire detection

equipment. However, for certain locations the

manual call points should be activated.

Having ascertained the location of the fire, check

out its severity and if local and contained, use

fire fighting equipment provided - hand

extinguishers, hose reels, etc.

If the fire cannot be extinguished within a few

minutes, the general alarm should be initiated

and the FIRE BRIGADE contacted. All plant

should be shut down.

Notes

Check the fire alarm is genuine and not

a fault.

4

The fire should be contained as far as possible,

without personal risks taken, until the fire

brigade has arrived.

The standard fire drill should be put

into operation. Check that all personnel

are evacuated from the immediate and

surrounding areas first, then from the

building completely.

Check that all windows in the

immediate and surrounding areas are

closed, together with all fire doors.

Beware of toxic fumes when in the

vicinity of fire. These are not

necessarily visible. If in any doubt,

abandon the attempt to fight the fire.

Remember, the gases are buoyant due

to heat, therefore, the air is more

breathable nearer floor level.

General Office Building, Reception Refurbishment

Section 3, Page 6

SECTION THREE

Title: Principles and Practice

Category: First Aid Procedures

a)          -            Definition

Emergency Procedures and First Aid

Item: 3.2.1

Page: 1 of 2

First Aid is based on the principles of practical medicine and surgery; a knowledge of the subject in case

of accident or sudden illness, enables trained persons to give such skilled assistance as will preserve life,

promote recovery and prevent the injury or illness becoming worse until medical aid has been obtained.

NOTE: Medical Aid indicates treatment by a Doctor.

First Aid consists of simple measures that anyone can learn but if carried out correctly, quickly, gently

and as early as possible, they can be life-saving.

b)          -            First Aider's Responsibility

This ends when handed over to the care of a Doctor, a Nurse or other responsible person, but not until they

have taken over the whole responsibility for the case. The First Aider should not leave until he has made

his report to the Doctor or other responsible persons and has ascertained whether he could be of any

further help.

First Aid, in general, is limited to the assistance rendered at the time of the emergency, with such material

as is available and often extensive improvisation will be necessary.

Remember at all times the importance of COMMON SENSE in First Aid, as an addition to the actual

knowledge of the subject. This section (and other First Aid Manuals) usually considers for treatment only

one condition at a time. However, in real life it will be found that serious accidents rarely produce a single

injury. Frequently, two injuries or more occur close together, so that the correct treatment of one may

interfere with the correct treatment of the other. One injury may require the casualty to be put on his back,

another that he should be in a coma or recovery position. In such a circumstance, the First Aider must

decide which injury is most serious, or needs the most urgent treatment and treat that one in the correct

way and then deal with the second injury as correctly as possible under the conflicting circumstances.

Often a casualty suffers from more than two injuries at the same time, which makes matters even more

difficult.

c)          -            The Scope of First Aid

This consists of three parts;

i)

ii)

iii)

Dealing with the situation, apart from the casualty.

Diagnosing what is the matter with the casualty and then giving the correct First Aid treatment.

Transferring of the casualty to a doctor, hospital or home and notifying those concerned about the

accident.

General Office Building, Reception Refurbishment

Section 3, Page 7

SECTION THREE

Title: Principles and Practice

Category: First Aid Procedures

In arriving at the diagnosis, the First Aider is guided by:

i)

Emergency Procedures and First Aid

Item: 3.2.1

Page: 2 of 2

ii)

iii)

The report furnished by persons present

(which includes the conscious casualty),

as to the cause of the injury or illness.

The account given by the casualty of their

own sensations and feelings.

The complete examination of the patient.

-

HISTORY

-

-

SYMPTOMS

SIGNS

d)

-

Priority in First Aid

Do first things first, quickly and methodically.

Check for danger.

Reassure the casualty and those around to lessen anxiety, whilst taking in the situation.

Ascertain from the casualty whether they are on any medication or have any medical conditions.

If breathing has stopped, start resuscitation.

Control visible bleeding.

Give priority to the individual with the most important injuries.

Give priority where several are injured to those who will benefit most by prompt treatment.

Guard against shock - and look for concealed bleeding.

Immobilise fractures.

Do not attempt too much - attend to the essential and prevent the condition from becoming worse.

Do not allow people to crowd around - they get in the way, and fresh air is essential.

Arrange early for careful conveyance of the casualty to Hospital or to a Doctor.

General Office Building, Reception Refurbishment

Section 3, Page 8

SECTION THREE

Title: Life Saving Measures

Category: First Aid Procedures

a)          -            Electrical Injuries

Emergency Procedures and First Aid

Item: 3.2.2

Page: 1 of 1

Even with domestic voltages, if an electric current passes through a person it may, in some cases, produce

stoppage of breathing, burns and cardiac arrest.

b)          -            Breathing Stopped

If the victim stops breathing he will die unless breathing is restored at once. First tilt his head back to open

the air passage from mouth to lungs, squeeze the nostrils together then blow your own breath through his

mouth into his lungs. If there is no improvement, it is likely that the heart has stopped beating and must

be restarted by compressing it by manual pressure in the chest wall.

c)          -            Bleeding

Bleeding from injuries must be controlled, as severe loss of blood may lead to death. The best way to stop

bleeding is to squeeze the injured part together BY DIRECT PRESSURE of the fingers on the wound, or

squeeze the edges of the wound together.

d)          -            Unconsciousness

The willing but untrained bystander is most helpless when confronted with the UNCONSCIOUS victim.

The simplest act of turning such a victim on his side, in the RECOVERY position, so that he cannot drown

in his own vomit, may save as many as 20% of such victims who would otherwise die.

e)          -            Shock

Shock is likely to be present in all cases of injury and many cases of sudden illness. Its effects, which may

be extremely serious, may be mitigated by the comfort, confidence and reassurance supplied by the

rescuer.

f)           -            Broken Bones

These are serious injuries - STOP ANY MOVEMENT OF BROKEN BONES which may make the injury

more severe. Injured limbs may be secured to the body or the other uninjured limb.

g)          -            Burns and Scalds

These are common injuries and if a large part of the body is involved, death may result. Cool the affected

area with cold water then cover with clean cloth or large dressing until seen by a Doctor.

General Office Building, Reception Refurbishment

Section 3, Page 9

SECTION THREE

Title: Emergency Situations

Category: First Aid Procedures

a)          -            The Situation

Emergency Procedures and First Aid

Item: 3.2.3

Page: 1 of 2

Be calm and take charge.

Ensure safety, i.e. from the possibility of falling masonry, etc.

Ask those present to remain, if considered responsible, as they may be able to help; otherwise they should

be requested to stand clear.

Give each one a specific job,

e.g.

Ring up and notify the Police.

Ask for an Ambulance or send for a Doctor.

(In each case, state the place of the accident and inform what has happened).

Ask if anyone has any First Aid knowledge.

Ask for help in turning the casualty or in steadying a limb.

(In each case, give exact instructions and if necessary show the bystander how your request should be

carried out).

b)          -            The Casualty

Depending on what has happened and the degree of severity of the injuries, decide whether to treat the

casualty where they are or whether to move them to a more suitable place.

If you decide to move him, carry out a quick preliminary examination of the head and neck, spine and four

limbs. Then decide on the most suitable method of removal in view of the injuries and the amount of

skilled and unskilled help available. Then complete theexamination of the casualty for injuries so that you

can make a complete diagnosis and carry out the necessary treatment.

c)          -            The Transferral

Stay with the casualty and reassure them until an Ambulance or Doctor arrives. Give your report to the

Doctor and if necessary accompany the Casualty to Hospital and report there. Notify the nearest relative

and any other person or organisation that should be told. In serious outdoor accidents the Police should

be sent for or notified.

General Office Building, Reception Refurbishment

Section 3, Page 10

SECTION THREE

Title: Emergency Situations

Category: First Aid Procedures

d)          -            Summary

THE MOST URGENT MATTERS ARE:-

1.

2.

3.

4.

Emergency Procedures and First Aid

Item: 3.2.3

Page: 2 of 2

5.

6.

Check for danger.

Get or send for help in accordance with current procedures.

To restart the heart if it has stopped beating.

To apply  resuscitation if the casualty  is not breathing. If in doubt as to whether the

casualty is alive or not, continue treatment until medical aid is available.

To control bleeding.

To maintain a clear airway by correctly positioning the casualty.

THE  MOST  IMPORTANT  PROCEDURES  TO  PREVENT  THE  CONDITION  BECOMING

WORSE ARE:-

1.

2.

3.

To dress wounds.

To immobilise fractures and to treat large wounds.

To place the casualty in the most comfortable position, consistent with the requirements

of treatment.

THE MOST HELPFUL MEASURES IN PROMOTING RECOVERY ARE:-

1.

2.

3.

4.

To relieve anxiety and promote confidence.

To relieve pain and discomfort.

To protect from cold.

To handle gently so as to do no harm.

General Office Building, Reception Refurbishment

Section 3, Page 11

SECTION THREE

Title: Dressings

Category: First Aid Procedures

a)          -            Purpose

Dressings are used to:-

i)

ii)

iii)

Assist in controlling bleeding.

To protect a wound from further injury.

To prevent or lessen infection.

Emergency Procedures and First Aid

Item: 3.2.4

Page: 1 of 1

An efficient dressing should be non-adherent and have a high degree of porosity.

b)

-

i)

ii)

Types of Dressings

Adhesive Dressings

The wound covering is of a non-adherent film which is supported by several layers of

absorbent gauze or cellulose held in place by a covering layer of adhesive material.

Sterilized dressings are sealed in a paper or plastic envelope and should not be opened

before use.

Bandages

Bandages are made from flannel domett (cotton and wool), calico, elastic net or paper.

They can be improvised from any of the above materials.

There are three different types;

a)

b)

c)

Triangular bandage

Roller bandage

Elastic net

c)

-

i)

ii)

iii)

iv)

v)

Purposes of Bandages

To retain dressings and splints in position.

To maintain direct pressure over a dressing to control bleeding.

To reduce or prevent swelling.

To afford support in the form of a sling.

To act as padding when nothing suitable is available.

General Office Building, Reception Refurbishment

Section 3, Page 12

SECTION THREE

Title: Treatment for Electric Shock

Category: First Aid Procedures

Emergency Procedures and First Aid

Item: 3.2.5

Page: 1 of 1

The following are the basic steps associated with treating a person who has suffered an electric shock:-

1)

2)

3)

4)

5)

Isolate the electrical supply.

Use a non-conducting material, such as wood, to pull the victim away from contact with live parts

or wires.

If the victim is not breathing, administer cardiopulmonary resuscitation (CPR) after breaking

contact with the electrical source.

Call a physician and continue CPR until breathing starts or until a physician arrives.

Treat an electrical burn as a thermal burn by applying clean, cold (iced) compresses. Prevent

contamination, and cover with a clean, dry dressing.

General Office Building, Reception Refurbishment

Section 3, Page 13

SECTION THREE

Title: Further Reading

Category: First Aid Procedures

Emergency Procedures and First Aid

Item: 3.2.6

Page: 1 of 1

The following books, published by St. John Ambulance Association, to which this section is indebted, are

strongly recommended for further information.

1)

2)

Digest of First Aid.

Authorised First Aid Manual.

Both of the above publications can be obtained from:-

St. John Ambulance Association and Brigade

1, Grosvenor Crescent,

London, SW1

General Office Building, Reception Refurbishment

Section 3, Page 14

SECTION FOUR

HEALTH AND SAFETY INFORMATION

SECTION FOUR

INDEX

ITEM

4.1

4.1.1

4.1.2

4.1.3

-

-

-

-

Health and Safety Information

DESCRIPTION

GENERAL

Introduction

Maintenance Policy

Causes and Avoidances of Accidents

GOOD PRACTICE

Introduction

Safe Working Conditions

Safe Way to Work

Personal Safety

Permit to Work

Warning and Safety Notices

General

SAFETY PROCEDURES AND CHECKS

Introduction

Personal Protection

Working with Electricity

Machinery

Tools and Clothing

Lifting and Access

Good Housekeeping

Fire Precautions

4.2

4.2.1

4.2.2

4.2.3

4.2.4

4.2.5

4.2.6

4.2.7

-

-

-

-

-

-

-

-

4.3

4.3.1

4.3.2

4.3.3

4.3.4

4.3.5

4.3.6

4.3.7

4.3.8

-

-

-

-

-

-

-

-

-

General Office Building, Reception Refurbishment

Section 4, Page 2

SECTION FOUR

Title: Introduction

Category: General

Health and Safety Information

Item: 4.1.1

Page: 1 of 1

This manual has been compiled within the framework of the Construction (Design and Management)

Regulations 1994, which place specific duties on Clients, Designers and Contractors to co-ordinate and

manage effectively the health and safety of workers and others throughout all stages of a construction

project from conception, design and planning through to the execution of works on site and subsequent

maintenance and repair.

It is intended that this manual forms part of the general Health and Safety file, the purpose of which is to

alert those responsible for the structure, after handover, to the health and safety risks that must be managed

when the structure and associated plant is maintained, repaired, renovated or demolished.

Health and safety issues are important in maintenance because statistics show the maintenance worker to

be at greater risk to accident and injury. This is partly because these workers are exposed to more hazards

than others, and partly because there are pressures of time and money upon the maintenance task to be

completed as quickly as possible. Less thought is given to the special needs for health and safety of the

maintenance task than is given to routine tasks which are easier to identify, plan and control.

General Office Building, Reception Refurbishment

Section 4, Page 3

SECTION FOUR

Title: Maintenance Policy

Category: General

Health and Safety Information

Item: 4.1.2

Page: 1 of 1

From the health and safety aspect, defects requiring maintenance attention, which have led, or could lead

to, increased risk to the workforce, should receive a high priority. Linking inspections with maintenance

can be useful so that work areas and equipment are checked regularly for present and possible future

defects. Some plant items are subject to statutory maintenance requirements as well as the manufacturers

requirements. These should all be strictly adhered to.

The need for maintenance of each piece of equipment has been anticipated in its particular design. The

overall maintenance of the complete system has been made safer by its consideration at the design and

later installation stage.

This manual contains all the information required to enable preventative and, when necessary, breakdown

maintenance being carried out, i.e. what action needs to be taken and how often. This particular section

contains details on good practice and special checks and procedures related to health and safety.

General Office Building, Reception Refurbishment

Section 4, Page 4

SECTION FOUR

Title: Causes and Avoidances of Accidents

Category: General

Health and Safety Information

Item: 4.1.3

Page: 1 of 1

Maintenance accidents are generally caused by one, or more, of the following factors:-

i)

ii)

iii)

iv)

v)

Lack of perception of risk by managers/supervisors, often because of lack of necessary training.

Unsafe, or no systems of work devised, e.g no permit to work systems in operation, no facility

to lock off machinery and electrics before work starts and until work has finished.

No co-ordination between workers or communication with other supervisors or managers.

Lack  of  perception  of  risk  by  workers,  including  the  failure  to  wear  protective  clothing  or

equipment, no co-ordination,

Use of maintenance contractors who are inadequately briefed on the health and safety aspects and

not selected on health and safety as well as cost grounds.

The  safe  operation  and  maintenance  of  systems  requires  steps  to  be  taken  to  control  the  causes  of

accidents. These steps can be divided into the following phases:

i)           Planning            -

ii)

Evaluation

-

iii)

Control

-

iv)

Monitoring

-

Identification  of  the  need  for  planned  maintenance  and  arranging  a

programme for this.

The hazards associated with each maintenance task should be listed and

the  risks  of  each  considered  (frequency  of  the  task  and  possible

consequences of failure to carry it out correctly). The tasks can then be

graded and the appropriate degree of management control applied to

each.

The control for each task will take the above factors into account, and

will include any necessary review of design and installation, training,

introduction of written safe working procedures to minimize risk, i.e. a

safe  system  of  work,  allocation  of  supervisory  responsibilities  and

necessary allocation of finances. Review of the activities of contractors

engaged in maintenance work will be required in addition.

Random checks, safety audits and inspections and the analysis of any

reported   accidents   for   cause,   which   might   trigger   a   review   of

procedures,constitutenecessary monitoringtoensurethecontrolsystem

is fully up to date. The introduction of any change in the workplace may

have maintenance implications and should therefore be included in the

monitoring process.

General Office Building, Reception Refurbishment

Section 4, Page 5

SECTION FOUR

Title: Introduction

Category: Good Practice

Health and Safety Information

Item: 4.2.1

Page: 1 of 1

It is the prudent duty of the employer to ensure, as far as is reasonably practicable, the health and safety

of the maintenance staff and other people using the premises. This section of the manual is a guide to some

of the precautions to be taken by both management and staff to achieve this.

The equipment and materials referred to in this section should be used, operated and maintained strictly

in accordance with the operating instructions or manufacturers' literature as appropriate.

It is the duty of every member of the maintenance team to take reasonable care for their own health and

safety and that of other people, who may be affected by their actions or omissions whilst at work. It is

strongly recommended that at least one copy of the Health and Safety at Work Act (1974) is available on

the premises and has been read and understood by all maintenance personnel.

Maintenance  staff  should  ensure  that  they  are  aware  of  and  understand  the  "IN  HOUSE"  rules  and

regulations which have been formulated and will incorporate safety precautions found to be necessary for

local conditions.

General Office Building, Reception Refurbishment

Section 4, Page 6

SECTION FOUR

Title: Safe Working Conditions

Category: Good Practice

Health and Safety Information

Item: 4.2.2

Page: 1 of 1

Work should not be carried out under conditions where there is an element of danger, if it is reasonably

practical to eliminate the risk. Safe working conditions should be provided to give protection and safe

ingress/egress where necessary. Work on live electrical circuits is not allowed.

Access doors and panels to all areas containing plant e.g. plant rooms, electrical panels, fan chambers etc.,

should be suitably identified and where appropriate carry warning notices.

Adequate ventilation should be provided. Special precautions should be taken where steam, smoke or any

other unhealthy or dangerous contaminants are present, particularly in confined spaces.

Lighting must be maintained at a high level in all plant rooms and service areas to enable inspections to

be carried out at any time, day or night and to avoid the risk of accident.

Ahighdegreeofcleanliness,both of rotatingmachinery andstaticequipment,isoftheutmostimportance.

Floorsandmachinery mustbeprotectedfrom spiltlubricantsandallloosematerials,containersandpapers

must not be allowed to accumulate.

General Office Building, Reception Refurbishment

Section 4, Page 7

SECTION FOUR

Title: Safe Way to Work

Category: Good Practice

Health and Safety Information

Item: 4.2.3

Page: 1 of 1

This can be summarised by a procedure which can be adopted for each maintenance risk.

Think about the dangers:

Check the task and site for hazards.

Decide on the precautions needed.

Prepare:

Put on safety clothing.

Assemble the tools and equipment.

Position DANGER and WARNING notices.

Erect safety barriers.

Position equipment in a safe place.

Carry out task:

Work in a logical sequence.

Use the correct tool for the job.

Never improvise on tools.

Discard defective tools.

Clear up after completion of task:

Collect all tools and equipment and return to store.

Remove notices or safety barriers.

Tidy up work area.

General Office Building, Reception Refurbishment

Section 4, Page 8

SECTION FOUR

Title: Personal Safety

Category: Good Practice

Health and Safety Information

Item: 4.2.4

Page: 1 of 1

The maintenance personnel must always use the protective clothing available. These items are the normal

requirement for the maintenance task.

Overalls or Dust Coats

Gloves

Rubber Boots

Face masks

Safety Shoes or Boots

Safety Glasses

Ear Protection

Safety Helmet

These must be worn at all times to protect the maintenance personnel

from dirt and spillage.

Reinforced non-slip, heavy duty industrial gloves must be worn when

handling heavy equipment, dirty or greasy items, or sharp edged metal

parts.

Must be worn when harmful chemicals are being handled, for example

stand-by battery supplies.

These must be worn when handling harmful chemicals.

Must be worn at all times. The reinforced sole and toe caps protect the

feet when walking on rough ground or moving heavy equipment.

These must be worn to prevent eye injuries, for example cutting wire or

cleaning sand and dust from equipment.

Must be worn in areas of high noise intensity, for example near diesel

generators or air compressors. The two main types are ear muffs and

earplugs.

Must be worn at all times when working in the site areas, underneath

any equipment, scaffolding or pipe runs or any other overhead hazard.

It should be noted that all safety helmets carry an expiry date and should

not be used after this time.

General Office Building, Reception Refurbishment

Section 4, Page 9

SECTION FOUR

Title: Permit to Work

Category: Good Practice

Health and Safety Information

Item: 4.2.5

Page: 1 of 3

A "Permit to Work" system must be adopted to meet and satisfy the legal requirements of the present

legislation, i.e. "Health and Safety at Work Act (1974)".

The "Permit to Work" system should incorporate the provisions listed below:

i)

ii)

iii)

iv)

v)

vi)

vii)

viii)

ix)

Before working on any items of equipment a "Permit to Work" docket, signed by an

appropriate authority, must be obtained. On completion of the work item, it should be

returned for "logging" in the master maintenance systems records.

To give authority to maintenance staff to commence inspection of plant, or to work on

plant.

To explain in outline the approach required to carry out the work in such a way that there

is no potential hazard to personnel or plant.

The system should be devised so that maintenance may be carried out safely and that no

starting up, or running, of plant presents an environmental hazard.

Co-ordination of staff requirements in relation to maintenance procedures and operations

to eliminate exposure of the work force to any hazard.

Correct  shutting  down  of  systems  must  be  implemented  and  no  electrical  work  on

equipment where removal of guards or housings has taken place, must be undertaken

without satisfactory clearance that the plant is now safe for work to be proceeded with.

Members of the maintenance staff must only carry out work within their discipline and

job description.

Where it is necessary to provide staging, scaffolding, towers and ladders to examine or

carry out replacement of components, then these must comply in all respects with the

latest legislation.

The authorized person will:-

a)

b)

Make sure all safety precautions are taken and recorded.

Enter on the work permit:-

-

-

-

What work has to be done.

What piece of equipment has to be made safe.

What safety precautions have been taken.

General Office Building, Reception Refurbishment

Section 4, Page 10

SECTION FOUR

Title: Permit to Work

Category: Good Practice

x)

Health and Safety Information

Item: 4.2.5

Page: 2 of 3

Maintenance tasks require strict adherence to safe working practices for the following

reasons:-

a)

b)

There will be a number of safety precautions.

Equipment close by may still be operating.

Notes on Permit to Work

Part 1 should be completed by the person authorising the work, before issuing to the person for the

switching, isolation, testing and earthing operations.Wherethepersonauthorisingthe work is responsible

for the switching etc., they should do this for themselves as a check on procedure.

Part 2 should be completed by the person responsible for the switching, isolating, testing and earthing

operations after their completion.

Part 3 both the original and duplicate should be signed by the person actually in charge of the work on the

apparatus. The original should be retained by the person actually in charge of the work until the work is

stopped or completed. The duplicate should be retained by the person authorising the work.

Part 4 should be signed by the person actually in charge of the work when the work has been stopped, or

completed, and then handed back to the person who authorised the work.

Part 5 should be signed by the person responsible for signing Part 2, or in their unavoidable absence, by

a person of equivalent status and understanding.

General Office Building, Reception Refurbishment

Section 4, Page 11

SECTION FOUR

Title: Permit to Work

Category: Good Practice

Example of Permit to Work

Permit to Work on Electrical Apparatus

Part 1 Authorization for Work.

A.

Health and Safety Information

Item: 4.2.5

Page: 3 of 3

No.........

B.

C.

D.

E.

This permit is issued for the following work   . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . .

. . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . .

By    . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . .  To  . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . .

being an authorised person in charge of switching and earthing operations.

Switching and Isolating. The apparatus to be disconnected from all live conductors by the following operation

Potential Tests and Earthing. Potential indicator test to be applied before fixing earths at the following points  .

Danger Notices are to be posted at:-    . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . .

Caution Notices are to be posted at:-   . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . .

Time  . . . . . . . . . . . . . . . . . . . . . . . . . . . . . .  Date . . . . . . . . . . Signed . . . . .    . . . . . . . . . . . . . . . . . . . . . . . .  Rank . . . . . .

Part 2 Declaration

I hereby declare that the operations in Part 1, B, C, D & E have been completed and apparatus detailed in Part 1, A, is

safe to work on, and any adjacent live equipment is securely padlocked. It will not again be made "live" until the

Clearance Certificate in Part 4 is completed.

ALL OTHER APPARATUS IS DANGEROUS

Time  . . . . . . . . . . . . . . . . . . . . . . . . . . . . . .  Date . . . . . . . . . . Signed . . . . .    . . . . . . . . . . . . . . . . . . . . . . . .  Rank . . . . . .

Part 3 Receipt

I hereby declare that I accept responsibility for doing the work on the apparatus detailed in Part 1, A, of this Permit and

that no attempt will be made by me or by men under my control to work on any other apparatus.

Time  . . . . . . . . . . . . . . . . . . . . . . . . . . . . . .  Date . . . . . . . . . . Signed . . . . .    . . . . . . . . . . . . . . . . . . . . . . . .  Rank . . . . . .

Part 4 Clearance of Work

This is to certify that the work detailed in Part 1, A above has been (stopped/completed)  * men, gear and tools withdrawn,

local earths removed.

Time  . . . . . . . . . . . . . . . . . . . . . . . . . . . . . .  Date . . . . . . . . . . Signed . . . . .    . . . . . . . . . . . . . . . . . . . . . . . .  Rank . . . . . .

( *Delete the word that does not apply.)

Part 5 Cancellation

I hereby declare this Permit to Work cancelled, and the earth connections applied at points indicated in Part 1, C, have

been removed. The apparatus is now ready for switching into service.

Time  . . . . . . . . . . . . . . . . . . . . . . . . . . . . . .  Date . . . . . . . . . . Signed . . . . .    . . . . . . . . . . . . . . . . . . . . . . . .  Rank . . . . . .

General Office Building, Reception Refurbishment

Section 4, Page 12

SECTION FOUR

Title: Warning and Safety Notices

Category: Good Practice

Health and Safety Information

Item: 4.2.6

Page: 1 of 1

The "The Health and Safety (Safety Signs and Signals) Legislation 1996" make it a legal requirement that

all safety signs comply with BS.5378: Part 1, 1980. BS.5378: Part 1, 1980 divides safety signs and notices

into four categories, according to the type of "Message". Each category has a distinctive colour and shape

as summarised below.

Sign Type

Colour

Shape

Outline circle with

cross bar

Solid circle

Meaning

a) You must not

b) Do not do

c) Stop

a) You must do

b) Carry out the action given by the sign

a) Caution

b) Risk of danger

c) Hazard ahead

a) The safe way

b) Where to go in an emergency

Prohibition

Red

Mandatory

Blue

Warning

Safe

Condition

Yellow

Outline triangle

Green

Rectangle

The following recommendations should be observed:-

i)

ii)

iii)

iv)

v)

At all times warning and safety notices must be maintained and properly displayed and worded

to give clear instructions.

Notices covering First Aid and Resuscitation from Electric Shock must be displayed in all plant

rooms.

Proper fire precautions must be observed within the plant rooms and building.

Notices must be displayed stating:-

NO SMOKING or SMOKING PROHIBITED IN THIS AREA

All fire fighting equipment must be clearly marked and available for use.

General Office Building, Reception Refurbishment

Section 4, Page 13

SECTION FOUR

Title: General

Category: Good Practice

a)          Escape Routes

i)

Health and Safety Information

Item: 4.2.7

Page: 1 of 1

b)

ii)

Keys

Periodic inspection of all escape routes, fire doors, fire exits., should be made to confirm

that doors open freely and routes are always kept clear of obstructions.

Should oil be spilt on bases or floors, the area must be thoroughly cleaned and sanded.

c)

d)

e)

Access to all plant rooms, electrical cupboards and equipment therein, which require a key to

open for access, should be controlled and restricted to authorised personnel only.

First Aid

First Aid boxes should be provided in accessible positions. These should be kept clean and in

good repair. Contents of the boxes should be regularly checked and missing items replaced.

Protective Clothing

Where  appropriate,  wear  protective  clothing  and  equipment,  i.e.  goggles,  respirators,  safety

harnesses. Protective screens should be provided when arc welding is in progress.

Drive Guards and Housings

Never work on moving parts of machinery. Exercise caution on the stationary parts. Ensure that

moving parts are protected by suitable guards. Be aware of warning notices such as:-

"Remotely Controlled Plant"

Do  not  put  hands  or  objects  on  any  item  of  stationary  rotating  machinery  as  this  may  start

automatically at any time.

WARNING:- Before commencing maintenance work on any item of plant, ensure the plant is

mechanically isolated from the system and that the electrical supply has also been isolated and

locked off. Ensure that all control and ancillary electrical circuits have been made safe.

f)

Replacement Parts

All safety  procedures are to be observed when using replacement parts, all electrical circuit

diagrams,manufacturers'spareslistsmustbecheckedagainsttheexistingequipment todetermine

it  is the correct arrangement or equipment for the specific application. Any  item used  must

comply with the correct British Standard Specification and where tests are carried out, they must

be in compliance with the relevant British Standard Specification or Code of Practice.

General Office Building, Reception Refurbishment

Section 4, Page 14

SECTION FOUR

Title: Introduction

Category: Safety Procedures and Checks

Health and Safety Information

Item: 4.3.1

Page: 1 of 1

The purpose of this list of safety procedures, is to provide general safety precautions to be used by persons

who own, install, operate, or maintain the systems described within this manual.

This list should not be used to replace instructions that are provided by the equipment manufacturer.

Therefore, anyone attempting to work on any equipment, should be thoroughly familiar with the specific

instructions for that particular unit.

The following is a list of the criteria that have been used here to indicate the intensity of the hazard:

DANGER

WARNING

CAUTION

SAFETY INSTRUCTIONS

-

-

-

-

This means that there is an immediate hazard that will

result in severe personal injury or death.

This means that hazards or unsafe practices could result

in severe personal injury or death.

This means that potential hazards or unsafe practices

could result in minor personal injury.

These  are  general  instructions  that  are  necessary for

safe working practices.

General Office Building, Reception Refurbishment

Section 4, Page 15

SECTION FOUR

Title: Personal Protection

Category: Safety Procedures and Checks

Warning

1.

2.

3.

4.

Health and Safety Information

Item: 4.3.2

Page: 1 of 1

Do NOT touch electrical wiring connections without first isolating the source of supply.

Do NOT touch electrical wiring connections with wet hands.

Do NOT touch electrical equipment while standing on a wet surface or wearing wet shoes.

Do wear a hard hat or other protection, when there is a possibility of falling objects.

Caution

1.

2.

3.

4.

5.

6.

7.

8.

9.

Do wear safety glasses equipped with side shields when working in workshops or at construction

sites.

Do  wear  gloves  when  handling  system  components  after  a  compressor  motor  burnout.  The

refrigerant and oil contain acid that can result in acid burns to the skin.

Do  wear  goggles  and  gloves  when  handling  chemicals;  when  welding,  cutting,  grinding  or

brazing; or when in an area where these operations are performed.

Do wear gloves and other protective clothing when working with sheet metal.

Do wear safety shoes when working around or lifting heavy objects.

Do wear protective clothing when arc welding to protect from serious burns.

Do wear ear protection when working in areas where sound levels are greater than 90db.

Do NOT wear jewellery, loose clothing, long ties, or gloves whilst working around moving belts

and machinery.

Do NOT wear rings or watches whilst working on electrical equipment.

Safety Instructions

1.

2.

Keep your work area clean of debris and free of liquid spills.

Do NOT continue working if you become ill. An unwell person is less observant and is therefore

more prone to accidents.

General Office Building, Reception Refurbishment

Section 4, Page 16

SECTION FOUR

Title: Working with Electricity

Category: Safety Procedures and Checks

Danger

1.          Do NOT attempt to check voltage without proper instructions.

Warning

1.

2.

3.

4.

5.

6.

7.

Health and Safety Information

Item: 4.3.3

Page: 1 of 1

Do NOT work on electrical circuits until they are opened, tagged, and locked.

Do NOT attempt to stop a unit by opening an isolating or fuse switch.

Do NOT attempt to check the resistance on an energised circuit.

Do NOT remove terminal box covers while a motor is running.

Do NOT handle capacitors until they have been properly discharged.

Do earth all electrical equipment.

Do use an earth fault current interrupter when using hand tools. (ie. RCD or RCBO).

Caution

1.

2.

3.

Do NOT bypass or block electrical circuit interlocks.

Do NOT check electrical equipment until you are certain that the electrical power is off in all

circuits.

Do use insulated fuse pullers on cartridge fuses.

Safety Instructions

1.

2.

3.

Do NOT store tools or parts in control or starter boxes.

Do NOT use meters for purposes other than those for which they have been designed.

Do  periodically  inspect  electrical  flex  and  replace,  or  repair,  any  damaged  flex,  plugs  or

connections.

General Office Building, Reception Refurbishment

Section 4, Page 17

SECTION FOUR

Title: Machinery

Category: Safety Procedures and Checks

Health and Safety Information

Item: 4.3.4

Page: 1 of 2

Before any machinery is worked on, it is essential that it is isolated and cannot be accidentally set in

motion. Procedures to ensure this are:-

a)

b)

c)

All isolation switches or circuit breakers are locked in the OFF position.

Warning notices stating:

MACHINE UNDER INSPECTION DO NOT SWITCH ON

displayed at the machine.

For major test and inspection the power supply must be disconnected.

Where ever possible the maintenance tasks must be performed on stationary machinery. In the exceptional

circumstances that this is not possible, GREAT CARE must be taken to avoid injuries and work must not

be carried out alone.

All live electrical terminals must be identified with warning notices stating:-

DANGER - LIVE ELECTRICAL PARTS

All guards, screens, shields, covers and lids must be secured with all screws or nuts and bolts, and warning

notices removed before the machinery is operated.

Guards - Types

Fixed Guards

Interlocked Guards

Automatic Guards

Trip Guards

Permanently  in  position  to  prevent  access  to  the  dangerous  parts  from all

directions.

Designed to remain in the closed position whilst machine is in motion.

Designed to remove the operator from danger.

Designed to stop the machine in case of danger.

General Office Building, Reception Refurbishment

Section 4, Page 18

SECTION FOUR

Title: Machinery

Category: Safety Procedures and Checks

Checks

Are all dangerous parts guarded?

Are all guards in good condition and properly secured?

Health and Safety Information

Item: 4.3.4

Page: 2 of 2

Does the guard prevent the operator, or anyone else, from reaching over or under into the dangerous part?

Are all the guards working properly?

Are the work feed openings of fixed guards small enough to prevent the operator from reaching through

to a dangerous part?

Are the start and stop controls easily accessible, in working order, and clearly identifiable?

Can the machine be positively isolated electrically?

How frequently are the guards or safety devices inspected or tested?

General Office Building, Reception Refurbishment

Section 4, Page 19

SECTION FOUR

Title: Tools and Clothing

Category: Safety Procedures and Checks

Health and Safety Information

Item: 4.3.5

Page: 1 of 1

The maintenance personnel must be prepared to go to any part of the site to carry out a task. It is not

always possible to take a complete tool kit, so careful forward planning is required. An incorrect tool must

never be used. The maintenance personnel must keep their tools in good working order. Any tool showing

signs of wear, damage or defect must be replaced.

Checks

Are the correct tools being used?

Are the handles secure?

Are the chisels and punches mushroom headed? (They should be ground smooth).

Are spanners being abused by the use of extension tubes?

Worn or defective tools should be disposed of and replaced.

Does all protective clothing fit correctly?

Do new employees have to wait for an issue of protective clothing?

Are visitors issued with protective equipment?

General Office Building, Reception Refurbishment

Section 4, Page 20

SECTION FOUR

Title: Lifting and Access Methods

Category: Safety Procedures and Checks

Health and Safety Information

Item: 4.3.6

Page: 1 of 1

To gain access to equipment it is often necessary for maintenance personnel to remove guards, screens,

shields, covers and lids.

All screws or nuts and bolts must be kept safe.

To gain access to equipment installed in difficult locations, maintenance personnel often need to erect

access equipment.

The  access  equipment  must  be  safe  and  secure,  footholds  and  handholds  must  be  provided  if  the

maintenance person is liable to fall more than two metres. This includes chains, ropes, slings, hooks, eye

bolts and shackles.

Checks

Is the lifting tackle being used correctly? Is the safe working load clearly marked?

Is the equipment being examined every six months?

Is there a certificate of test showing the safe working load?

Is the ladder secured at the top? If not, is it firmly fixed at the bottom or footed by a second person?

Is the ladder erected with the appropriate height/distance from wall ratio?

Is the ladder in good condition, no missing or improvised rungs?

How frequently are the ladders inspected?

General Office Building, Reception Refurbishment

Section 4, Page 21

SECTION FOUR

Title: Good Housekeeping

Category: Safety Procedures and Checks

Health and Safety Information

Item: 4.3.7

Page: 1 of 1

Maintenance work is not always possible under ideal conditions, for example, working above ground or

in confined spaces. It is therefore essential that a tidy area, clear of obstructions and loose tools, is kept

during the maintenance task.

Checks

Is there a place for everything and is everything in its place?

Are gangways, aisles, passageways and stairs kept clear and free from substances likely to cause a person

to slip?

Is the lighting satisfactory?

Are handrails provided on stairs?

What is the system for cleaning up spillage of materials or substances?

Are all floors and stairs in good repair?

Are potentially harmful substances used in your workplace, if so:-

i)

ii)

iii)

iv)

Are they clearly marked with instructions as to how they should be used, stored and

disposed of?

Are the employees trained in their use?

Is the workplace adequately ventilated?

What is the system for dealing with an emergency, in relation to those substances?

Hot, Scalding or Corrosive liquids may be used in the workplace:-

i)

ii)

Are the tanks containing these liquids, fenced to a height of 4 metres or securely covered?

Are any gangways above the tanks provided with adequate guard rails?

Have all Control of Substances Hazardous to Health (COSHH) requirements been met?

General Office Building, Reception Refurbishment

Section 4, Page 22

SECTION FOUR

Title: Fire Precautions

Category: Safety Procedures and Checks

Health and Safety Information

Item: 4.3.8

Page: 1 of 1

Are the quantities of highly flammable liquids stored in the workroom, kept to a minimum?

Are the empty containers and contaminated rags etc., removed immediately from the work place?

Are there any naked flames or any other possible sources of ignition present when using flammable

liquids?

Is smoking prohibited, and if so, is the rule being observed?

Are all the extinguishers in their correct position, full and free from obstruction?

Are all the gangways and staircases which may be used as a means of escape, free from obstruction?

Can every door along the escape route be easily and immediately opened from inside?

Have fire resisting or smoke stop doors been wedged open?

Can the Fire Alarm be heard in all parts of the work place?

Has the fire alarm been tested during the last three months?

When was the last fire evacuation drill?

What potentially hazardous dusts are used in your work place?

What safeguards are used to minimise risk?

General Office Building, Reception Refurbishment

Section 4, Page 23

SECTION FIVE

OPERATING PROCEDURES

SECTION FIVE

INDEX

ITEM

5.1

5.1.1

-

-

Operating Procedures

DESCRIPTION

GENERAL

Introduction

5.2

5.2.1

-

-

FILLING PROCEDURES

Direct Expansion Air Conditioning Systems

5.3

5.3.1

-

-

DRAINING PROCEDURES

Direct Expansion Air Conditioning Systems

General Office Building, Reception Refurbishment

Section 5, Page 2

SECTION FIVE

Title: Introduction

Category: General

Operating Procedures

Item: 5.1.1

Page: 1 of 1

The procedures in this section are laid out on a step-by-step basis. No step within the procedure should

be taken unless the preceding step has been satisfactorily completed, unless otherwise stated. Before

carrying out any procedure it should be read through to ensure that it is completely understood and that

any tools, equipment, spares etc., required, are to hand. Additionally, the relevant descriptions and plant

data should be read for familiarisation of the particular system to which the procedure refers.

The  building services have been generally  designed for automatic operation. The systems are inter-

dependant on each other and, therefore, should not be treated in isolation in the normal operation of the

building.

General Office Building, Reception Refurbishment

Section 5, Page 3

SECTION FIVE

Title: Direct Expansion Air Conditioning Systems

Category: Filling Procedure

Operating Procedures

Item: 5.2.1

Page: 1 of 1

Description: This describes the filling procedure for a direct expansion air conditioning system.

Notes:

1. The following works should only be carried out by a qualified refrigeration engineer using the

correct items of equipment.

Step

1

2

3

4

5

6

7

Action

Carry out a pressure test of the complete

refrigeration pipework system.

Upon completion of a pressure test, release the

pressure very carefully and remove test

equipment.

Fit evacuation equipment to the pipework and

evacuate the lines to remove all air, condensation

etc.

During the evacuation period check over the

equipment to ensure all components are ready to

operate.

Remove evacuation equipment and fit refrigerant

gas canister leads to pipework. Switch on main

electrical supply and begin the filling of the

system.

Upon completion of the filling operation remove

the gas canister leads and check the operation of

all equipment and controls.

Ensure that crankcase heater is functional and

leave system for a minimum of eight hours

before putting into operation.

Notes

Refer to the manufacturers' literature for

pressure limits.

Care should be taken when releasing the

high pressures involved.

Refer to manufacturers' literature for the

quantity of gas to be used.

8

Finally check the function of all controls.

This period allows the heater to reach

its operating temperature and the gas to

settle.

The system is now ready to operate

under the dictates of the controls

system.

General Office Building, Reception Refurbishment

Section 5, Page 4

SECTION FIVE

Title: Direct Expansion Air Conditioning System

Category: Draining Procedure

Operating Procedures

Item: 5.3.1

Page: 1 of 1

Description: This describes the procedure for draining a direct expansion air conditioning system.

Notes:

1. The following works should only be carried out by a qualified refrigeration engineer using the

correct items of equipment.

Step

1

Action

Switch off controls operation.

Fit refrigerant gas collection canister leads to the

pipework and draw off the refrigerant.

Upon completion of the degassing process,

disconnect leads, close valves and remove

collection unit.

Switch off local isolators and main electrical

supply.

Notes

2

3

4

All refrigerant must, by law, be

removed for proper recycling or

disposal if contaminated.

This ensures that the crankcase heater is

taken off line.

General Office Building, Reception Refurbishment

Section 5, Page 5

SECTION SIX

MAINTENANCE SCHEDULES

SECTION SIX

INDEX

ITEM

6.1

6.1.1

-

-

Maintenance Schedules

DESCRIPTION

GENERAL

Introduction

6.2

6.2.1

6.2.2

6.2.3

6.2.4

6.2.5

6.2.6

6.2.7

6.2.8

-

-

-

-

-

-

-

-

-

COOLING SYSTEMS

Direct Expansion Air Conditioning Unit

Compressor

Filter (Panel Washable)

Cooling Coil (DX)

Fan

Small Fan

Electric Motor

Insulation

General Office Building, Reception Refurbishment

Section 6, Page 2

SECTION SIX

Title: Introduction

Category: General

Maintenance Schedules

Item: 6.1.1

Page: 1 of 1

Only a regular and organised scheme of maintenance work, planned, to cover all details of the installation,

within given maintenance periods, can ensure continued satisfactory operation with a minimum liability

tointerruptionstosupply duetoequipmentfaults.Aplannedmaintenanceschemeshouldincludeasystem

of logging, wherein records are kept of inspection, maintenance and repair of all items of plant and

equipment.

Careful attention must be given to securing the safety of personnel and equipment while maintenance or

repair work is in progress. A code of safety rules based on a system of "permits to work" is recommended.

Plant rooms should be kept clean and the practice of using plant room space for storage must not be

permitted.Accesstoplantroomsandequipmentmustbelimitedtoauthorisedpersonnelwhoaremembers

of the engineering staff.

Where  maintenance  work  is  in  progress,  a  DANGER  notice  must  always  be  attached  to  any  "live"

apparatus calling attention to the danger of approach. A CAUTION notice must always be attached to

plant or its associated control equipment which may be occasioned by interference. Before any work is

commenced on any item of equipment, the supply and ancillary circuits must be isolated and locked off

if possible.

All safety precautions and general recommended procedures relating to the maintenance of switchgear are

contained  in  the  British  Standard  CP5405  (1976)  and  this  should  be  read  in  conjunction  with  the

instructions for routine periodic maintenance given in the following pages.

General Office Building, Reception Refurbishment

Section 6, Page 3

SECTION SIX

Title: Direct Expansion Air Conditioning Unit

Category: Cooling Systems

Item     Frequency

Maintenance Schedules

Item: 6.2.1

Page: 1 of 1

1

2

3

4

5

6

7

8

Monthly

3 Monthly

9

Various

1

2

3

4

5

6

7

8

3 Monthly

9

Various

Details

Internal Unit

Remove and clean return air filter.

Clean surfaces of casing.

Brush or vacuum clean evaporator coil

surfaces.

Check for correct operation of controls.

Check fan is free to rotate.

Check for unusual noise or vibration.

Clean out drip tray and ensure condensate

drain is free from obstruction.

Check unit for signs of leakage.

Check and maintain component items -

refer to individual component's

maintenance schedule.

External Unit

Inspect unit for signs of leakage or

corrosion.

Clean condenser coil surfaces.

Check fans are free to rotate and impellers

are secure onto shaft.

Check operation of all controls.

Check refrigerant charge.

Check operation of crankcase heater.

Check crankcase oil level.

Check for unusual noise or vibration.

Check and maintain component items -

refer to individual component's

maintenance schedule.

Notes

Brush clean or wash in warm

soapy water.

Small Fan, Coil, Filter

(Washable Panel)

Clean off any deposits and treat

any bare metal accordingly.

Top up as required.

Top up as required.

Fan, Coil, Compressor

General Office Building, Reception Refurbishment

Section 6, Page 4

SECTION SIX

Title: Compressor

Category: Cooling Systems

Item

1

2

Frequency

Details

Check compressor for signs of leakage.

Check oil level.

Maintenance Schedules

Item: 6.2.2

Page: 1 of 1

Notes

3

Weekly

Check if oil is contaminated with

refrigerant.

4

Check for unusual noise or vibration.

5

6

Yearly

7

Various

Inspect compressor for signs of corrosion.

Check security of electrical connections.

Check and maintain component items -

refer to individual component's

maintenance schedule.

This can be viewed through the

sight glass. Top up as required.

Excessive foaming will indicate

the presence of refrigerant.

Switch off unit and investigate

cause.

Internal components may be

broken. Overhaul or replace as

necessary.

Remove rust etc and treat any

bare metal accordingly.

Electric Motors.

General Office Building, Reception Refurbishment

Section 6, Page 5

SECTION SIX

Title: Filter (Panel Washable)

Category: Cooling Systems

Item     Frequency

Maintenance Schedules

Item: 6.2.3

Page: 1 of 1

1

Monthly

Details

Take manometer reading. If reading

shows the filter cells are at their

maximum pressure drop they should be

washed. After washing check condition of

filter medium, if damaged replace.

2

Wipe any accumulated dirt from the

retaining channels and frames.

Notes

Refer to the Plant Data.

Check cells are replaced in the

correct direction for air flow.

On replacing access doors check

that the integral seals give a

good air seal. If not, replace

seals.

General Office Building, Reception Refurbishment

Section 6, Page 6

SECTION SIX

Title: Cooling Coil (DX)

Category: Cooling Systems

Item

1

Frequency

Monthly

Maintenance Schedules

Item: 6.2.4

Page: 1 of 1

2

3 Monthly

3

Details

Check pipework connections for leaks.

Check coil matrix is clean, unobstructed

and air flow is evenly distributed over

coils.

Check condensate drain pans and

connections are clear. Check drain pipe is

properly attached.

Notes

4

6 Monthly

Clean coil matrix.

5

Yearly

Check air pressure drop across coil.

Use soft brush and mild

detergent solution. If heavily

contaminated with grease use

steam lance. Take care not to

damage or distort fins.

Refer to the Plant Data.

General Office Building, Reception Refurbishment

Section 6, Page 7

SECTION SIX

Title: Fan

Category: Cooling Systems

Item

1

Frequency

Daily

Maintenance Schedules

Item: 6.2.5

Page: 1 of 1

2

Weekly

3

4

Monthly

5

6

7

6 Monthly

8

9

Yearly

10

Various

Details

Check fan is running smoothly without

excessive noise or vibration.

Check flexible connections are secure,

taut and airtight.

Check that fan guard is clean and

unobstructed.

Check anti-vibration mountings/hangers

are secure, free to move and in good

condition.

Check anti-back draught damper

operation (air tightness and freedom of

movement).

Check impeller and shaft for freedom of

movement and balance.

Check impeller and blades. Check

security of impeller on shaft and inspect

blades for security and damage.

Check performance of fan (shaft speed,

air velocity and pressure).

Clean and check casing internally and

externally, repairing any corrosion or

damage to finish found. Check all bolted

joints are secure.

Check and maintain component items -

refer to individual component's

maintenance schedule.

Notes

Connections must not resist air

flow.

Refer to the certificates and the

Plant Data.

Electric Motor

General Office Building, Reception Refurbishment

Section 6, Page 8

SECTION SIX

Title: Small Fan

Category: Cooling Systems

Item

1

Frequency

3 Monthly

Maintenance Schedules

Item: 6.2.6

Page: 1 of 1

2

6 Monthly

3

4

Yearly

5

6

Various

Details

Clean intake and discharge grilles.

Remove grille and motor/impeller

assembly and clean inner surfaces of

casing.

Vacuum clean motor/impeller assembly.

Refit motor/impeller assembly and grille.

Remove grille and motor/impeller

assembly. Strip down motor/impeller

assembly and clean all items.

Apply a few drops of mineral oil to motor

bearings. Refit motor/impeller assembly

and grille.

Check and maintain component items -

refer to individual component's

maintenance schedule.

Notes

Brush off any debris and wipe

with a damp cloth.

Wash all non-electrical

components in warm soapy

water. Ensure all items are dried

thoroughly.

Electric Motor

General Office Building, Reception Refurbishment

Section 6, Page 9

SECTION SIX

Title: Electric Motor

Category: Cooling Systems

Maintenance Notes

(a)

Maintenance Schedules

Item: 6.2.7

Page: 1 of 1

(b)

Always ensure the electrical supply to the motor is positively isolated before carrying out any

work. Do Not rely on a local lockstop button for isolation.

Unless specifically designed for it, electric motors are extremely susceptible to the effect of

extremes of temperature, dust and moisture. Every care must be taken to ensure they operate in

a clean and dry environment.

Frequency

Notes

Item

1

Monthly

2

3

3 Monthly

4

5

6

6 Monthly

7

3 Yearly

Details

Generally check motor to ensure casing

ventilation louvres are unobstructed,

alignment is correct, holding down bolts

and pulley/couplings are secure, and

motor runs without excessive vibration,

temperature or noise.

Totally enclosed motors only - Check that

casing drain holes are unobstructed or if

plugged, remove plugs to drain off any

accumulated condensation.

Check motor terminals are secure, cables

show no signs of overheating, terminal

box is internally dry and clean, and cover

is refitted securely.

Intermittently running motors subjected to

damp conditions - Check that insulation

resistance across winding is at an

acceptable value.

Single phase motors only - Check

centrifugal switch for wear and action.

Check drawn full load current does not

exceed value stated on name plate and as

detailed in the Plant Data.

Dismantle and overhaul motor in

accordance with manufacturers

recommendations.

Positively isolate motor before

carrying out this check.

Note measured current drawn

for future reference and

comparison.

This should be carried out by a

specialist.

General Office Building, Reception Refurbishment

Section 6, Page 10

SECTION SIX

Title: Insulation

Category: Cooling Systems

Item

1

2

Frequency

6 Monthly

Yearly

Details

Inspect outer surfaces for damage. Repair

or replace as necessary.

Check integrity of vapour seals.

Maintenance Schedules

Item: 6.2.8

Page: 1 of 1

Notes

General Office Building, Reception Refurbishment

Section 6, Page 11

SECTION SEVEN

MAINTENANCE INSTRUCTIONS AND LOG BOOKS

SECTION SEVEN

INDEX

ITEM

7.1

7.1.1

7.1.2

7.1.3

-

-

-

-

Maintenance Instructions and Log Books

DESCRIPTION

INTRODUCTION

Formulation of a Planned Maintenance Programme

Energy Usage Log Books

Maintenance Log Books

RISK ASSESSMENTS

Working Alone

Working in Occupied Premises

Working in Confined Spaces

Working at Heights

Use of Ladders

Use of Trestles

Use of Hand Tools

C.O.S.H.H. INSTRUCTIONS

Introduction

Refrigerant Gas

Foam Insulation

SAMPLE LOG BOOKS

General Maintenance Log Book

7.2

7.2.1

7.2.2

7.2.3

7.2.4

7.2.5

7.2.6

7.2.7

-

-

-

-

-

-

-

-

7.3

7.3.1

7.3.2

7.3.3

-

-

-

-

7.4

7.4.1

-

-

General Office Building, Reception Refurbishment

Section 7, Page 2

SECTION SEVEN

Title: Formulation of a Planned Maintenance Programme

Category: Introduction

Maintenance Instructions and Log Books

Item: 7.1.1

Page: 1 of 1

This Operating and Maintenance Manual is designed for use by "In-House" maintenance personnel and

it is recommended that a Planned Maintenance Programme is formulated to ensure the safe and efficient

operation of the plant and systems installed.

It is also recommended that a log book of any preventative maintenance tasks, faults and subsequent

corrective maintenance tasks carried out, is kept. This will provide any new maintenance personnel with

a history of the systems installed and highlight key areas that may require attention.

Thefollowingschedulesincorporatetwotypesofmaintenance,firstly thehighfrequency items aremainly

checks to ensure that the plant and systems are operating correctly. Secondly, the lower frequency items

mainly consist of preventative maintenance tasks to ensure that the plant and system continue to operate

in a safe and efficient manner.

In the formulation of a Planned Maintenance Programme, it is important to identify those items which are

simply checksand thosewhich arepreventativemaintenancetasks.Althougheachindividual maintenance

schedule needs to be read and understood before this can be determined, a general rule (which will not

apply in all circumstances) can be applied. All items with a frequency greater than one month are checks

and any items with a frequency less than one month are maintenance tasks. Items with a frequency of one

month will vary from one item of equipment to the next and the general rule cannot be applied here.

Although the frequency of the preventative maintenance task is specified, the careful scheduling of the

maintenance needs to be made to minimise any inconvenience caused to the building occupier.

General Office Building, Reception Refurbishment

Section 7, Page 3

SECTION SEVEN

Title: Energy Usage Log Books

Category: Introduction

Maintenance Instructions and Log Books

Item: 7.1.2

Page: 1 of 1

The effective implementation of a planned preventative maintenance regime, as outlined within previous

sections of this document, would be incomplete without the monitoring of energy usage as outlined within

the Building Regulations, Part L2, Conservation of Fuel and Power (2006 Edition).

As detailed within the above regulation, suitable metering for this building will have been included within

thesystemsatthedesignconceptionstage,togetherwithestimatednormalenergy usagecalculations.This

information, updated to incorporate changes following system alteration, should be used as a baseline

comparison to the continual log of energy usage. Any discrepancies found, either higher or lower than the

estimated energy usage, should be investigated and if necessary remedial action taken. For example,

higher than normal usage could indicate, leaks, insulation damage or faulty equipment.

NOTE: It must be remembered that such comparisons of baseline figures to actual readings have little

meaning with regard to day-to-day usage. Only average figures over years/months should be used

to highlight potential problems and changes to system operation.

General Office Building, Reception Refurbishment

Section 7, Page 4

SECTION SEVEN

Title: Maintenance Log Books

Category: Introduction

Maintenance Instructions and Log Books

Item: 7.1.3

Page: 1 of 1

In addition to the energy usage logs, a general log of preventative and remedial maintenance, should also

be kept to assist with the diagnosis of potential problems and to provide a history of maintenance for

future personnel. The exact arrangement of this maintenance log will be dependant on the preferences and

regime implemented by the maintenance personnel, however, a logical approach to the record keeping is

essential, particularly to cater for staff changes.

There are three main options with regards to the structure of record keeping as follows:-

1)

2)

3)

Chronological

System by System

Equipment Basis

All maintenance actions are recorded in chronological order.

Separate log books are kept for each system.

Separate log books are kept for each item of equipment.

The advantages/disadvantages of each approach are summarised in the following table:-

Type

Chronological

Advantages

Extremely simple and compact method

of keeping records.

System

Equipment

Historical comparison and

identification of potential problems

easily achieved.

Greatest flexibility regarding historical

comparison.

Disadvantages

Locating historical information for any

given item of equipment could prove

difficult.

Slightly more complex and bulky

system of keeping records than the

simple chronological approach.

No more complex than the system

approach, however, "documentation

overload" could occur due to the sheer

amount of paperwork being kept. Cross

references between one item of

equipment and another on the same

system could prove difficult to

maintain.

General Office Building, Reception Refurbishment

Section 7, Page 5

SECTION SEVEN

Title: Working Alone

Category: Risk Assessments

Maintenance Instructions and Log Books

Item: 7.2.1

Page: 1 of 1

Assessment of Risk

Low

Medium

3

3

High

Description of Risk

Falling from a height

Electric shock

Planning

Physical

Managerial

Training

Actions to be Taken to Minimise the Risk

Correct planning should include an assessment of the work, so that the likelihood of

injury and the possible consequences to the lone worker are considered. Where there

are hazardous substances, live electrical work, the need to work at height or near

water, lone working should be avoided.

Lone worker alarms or other means of communication should be provided. First aid

facilities to treat minor injuries should be available during work periods and those

working alone should be advised of their location. Suitable means of access should

be provided which can be handled safely by one person.

Peripatetic workers should be supervised on a regular basis and management should

ensure that their whereabouts are known at all times. Only experienced and trained

operatives, with no adverse medical history, should be considered for working alone.

The permitted limits of work and the limits on the initiative of the individual should

be clearly specified before work is authorised.

Levels of training and experience for lone workers should include a full

understanding of the work involved, together with a thorough knowledge of the

hazards and emergency procedures. Workers should also clearly understand the

limits of the work which have been authorised and the limits on their own initiative.

General Office Building, Reception Refurbishment

Section 7, Page 6

SECTION SEVEN

Title: Working in Occupied Premises

Category: Risk Assessments

Maintenance Instructions and Log Books

Item: 7.2.2

Page: 1 of 1

Assessment of Risk

Low

Medium

3

3

3

3

High

Description of Risk

Electric shock/burns

Fire

Falling from heights

Injuries to third parties - falls

Injuries to third parties - falling objects

3

Planning

Managerial

Training

Actions to be Taken to Minimise the Risk

Planning should include the exchange of information with owner/occupier to ensure

full reciprocal knowledge of existing hazards, demarcation of areas of responsibility

and work hazards. Access equipment should be provided to ensure the maximum

safety of workers and occupants. Details of existing services should be obtained

before the commencement of works and COSHH and noise assessments should be

available for materials and tools to be used. Physical barriers and notices should be

installed to isolate work from occupants and members of the public. Fire exit routes

should be kept free from obstruction and alternate routes should be clearly signed.

Hot work should be controlled and extinguishers on hand. Where work at height

needs to be carried out, debris netting, fans or other suitable measures to protect the

public should be installed. Flammable and hazardous materials should be correctly

controlled and stored.

Supervisors should monitor all works, carrying out initial checks to ensure that safe

systems of work are in place before commencement and that areas are left safe at the

end of each work period. Regular liaison should take place with occupants to co-

ordinate work and eliminate hazards to them. Use of personal protective equipment

and ventilation equipment should be monitored to ensure compliance with COSHH

assessments.

Induction training should include any hazards and necessary precautions required for

the workplace. Operative training should include safe systems of work and

precautions designed to prevent injury to third parties. Supervisory management

should be trained in site safety supervision.

General Office Building, Reception Refurbishment

Section 7, Page 7

SECTION SEVEN

Title: Working in Confined Spaces

Category: Risk Assessments

Maintenance Instructions and Log Books

Item: 7.2.3

Page: 1 of 1

Assessment of Risk

Low       Medium

High

3

3

3

3

Description of Risk

Poisoning from toxic gases

Asphyxiation - lack of oxygen

Explosion

Fire

Excessive heat

Drowning

3

3

Planning

Physical

Managerial

Training

Actions to be Taken to Minimise the Risk

Planning should eliminate the need for entry or use of hazardous materials by the

selection of alternative methods of work or materials. An assessment of the

ventilation available and possible local exhaust ventilation requirements should be

made, together with the potential presence of hazardous gases/atmosphere, process

by products and the need to improve hygiene/welfare facility.

A documented entry system should be applied, preferably a Permit to Work System

and adequate ventilation should be present. Detection equipment should be present

before entry to check on levels of oxygen and presence of toxic or explosive

substances. The area should be tested before entry and continually whilst any person

is in the confined space. Breathing apparatus or airlines should be provided if local

ventilation is not possible. Where no breathing apparatus is assessed as being

required, emergency breathing apparatus and rescue harnesses should be provided.

Rescue equipment, including lifting equipment, resuscitation facilities, safety lines

and harnesses should be provided and a communication system with those in the

confined space should be established. Air should not be sweetened with pure oxygen

and precautions for the safe use of any plant or heavier-than-air gases in the confined

space should be established before entry. Necessary personal protective equipment

and hygiene facilities should be provided for those entering sewers.

The management's role should be to decide on the nature of the confined space and

put a safe system into operation, including checking the above. Flood potential and

isolations should be checked.

Full training should be provided for all persons entering and managing confined

spaces. A surface rescue party should be trained in first aid procedures and the

operation of testing equipment. All operatives and supervisory staff should be

certified as trained to the same standard.

General Office Building, Reception Refurbishment

Section 7, Page 8

SECTION SEVEN

Title: Working at Heights

Category: Risk Assessments

Maintenance Instructions and Log Books

Item: 7.2.4

Page: 1 of 1

Assessment of Risk

Low

Medium

3

High

Description of Risk

Falls of persons

Falls of materials

3

Planning

Physical

Managerial

Training

Actions to be Taken to Minimise the Risk

Work should be planned to ensure that a safe means of access is provided. Reference

should also be made to the use of access equipment. All equipment should be

provided and maintained to the required legal standards..

Suitable signs and barriers should be positioned directly below the works to warn of

overhead operations. Edge protection should be erected at places of work, where

falls of more than 2 metres could occur. Where edge protection is removed for

access, or is not reasonably practicable, personal suspension equipment should be

used by operatives working at or near the edge. Where there is likely to be falling

debris, chutes or full enclosures should be used to protect third parties. All operatives

working below overhead operations should wear safety helmets.

All equipment used should be checked to ensure it is in good order, to correct

specification and in date for inspection. Work should be monitored to ensure that

additional precautions and equipment is taken into use if edge protection is removed.

Other relevant British Standards include: BS 7883:1997 - Anchors for Safety

Harnesses, BS 8213 Part 1:1991 - Code of Practice for Cleaning of Windows and

Doors, BS EN 355, 358, 361-365 - Personal Protective Equipment Against Falls

from a Height.

Training and instruction should be provided to all operatives and supervisory staff

involved in the use of suspension equipment, such as lines and harnesses and how to

inspect and assess personal protective equipment of this type before use.

General Office Building, Reception Refurbishment

Section 7, Page 9

SECTION SEVEN

Title: Use of Ladders

Category: Risk Assessments

Maintenance Instructions and Log Books

Item: 7.2.5

Page: 1 of 1

Assessment of Risk

Low

Medium

3

3

High

Description of Risk

Falls of persons from ladders

Ladder slipping

Objects dropping by ladder user

3

Planning

Physical

Managerial

Training

Actions to be Taken to Minimise the Risk

Ladders should be checked to ensure correct length, type and condition before use

and should be subject to a planned maintenance programme. Ladder work should be

restricted to that which can be carried out using one hand only and will only take

twenty minutes to complete.

The ground base for the ladder should be firm and level. The ladder should be of

sufficient length to extend a sufficient height above the step-off point when used as

access to a scaffold. The correct angle of rest for a ladder is 75 degrees, or a base to

height ratio of 1:4. Ladders should be secured against slipping, by tying at the top or

the bottom. Ladders should only be footed as a sole precaution against movement if

less than 3 metres high. Overreaching from ladders should be avoided. When using

stepladders the hips should be kept below the top platform and between the stiles to

ensure stability.

Supervisors should check ladders before use to ensure they are sound. Use made of

ladders should be monitored regularly, to ensure that operatives are not overreaching

or using two hands to work. Damaged ladders should be broken up or removed from

the workplace immediately. Painted ladders should not be accepted for use.

Managers should check method statements supplied by sub-contractors and others,

e.g. window cleaners, to ensure that ladders will be used correctly and that safe

access will be available.

All operatives should be trained in the safe use of ladders and the hazards which

must be avoided. This should be done at induction.

General Office Building, Reception Refurbishment

Section 7, Page 10

SECTION SEVEN

Title: Use of Trestles

Category: Risk Assessments

Maintenance Instructions and Log Books

Item: 7.2.6

Page: 1 of 1

Assessment of Risk

Low

Medium

3

3

High

Description of Risk

Falls of persons and materials from working platform

Collapse of trestles

Planning

Physical

Managerial

Training

Actions to be Taken to Minimise the Risk

Lightweight staging or mobile access scaffold should be used in preference to

trestles. Trestles should only be planned for light work of relatively short duration.

Lightweight staging should be used in preference to boards and be positioned so that

at least one-third of the height of the trestle is above the platform. Staging/platform

width should be at least 600mm. Toe-boards and guardrails are required to platforms

above 2 metres in height.

All equipment used should be checked to ensure it is in good order before use, to

ensure no loose or damaged cross bearers, the hinges are in good order and that there

are no defective stiles (loose or missing bolts or screws). Management should

supervise the use of trestles to ensure that operatives moving and erecting trestles are

properly trained and instructed and that those using trestles do not overreach.

Training and instruction should be provided to all operatives and supervisory staff

involved in the use of trestles as above.

General Office Building, Reception Refurbishment

Section 7, Page 11

SECTION SEVEN

Title: Use of Hand Tools

Category: Risk Assessments

Maintenance Instructions and Log Books

Item: 7.2.7

Page: 1 of 1

Assessment of Risk

Low

Medium

3

High

Description of Risk

Eye Injury

Injury to hands, feet and body

3

Planning

Physical

Managerial

Training

Actions to be Taken to Minimise the Risk

Tools provided by the employer should be assessed to ensure they are fit for the

environment in which they are to be used and in good working condition. Tools are

required to be suitable for the purpose for which they will be used.

Eye protection should be provided and used whenever work is carried out using cold

chisels, drills, grinders or other tools where there is a risk of flying particles or pieces

of the tool breaking off. Open-bladed knives, screwdrivers and other sharp tools

should be carried and used so as not to cause injury to the user or others. Non-ferrous

(spark-free) tools should be used in flammable atmospheres. Insulated tools should

be used where there is a possibility of live electrical work.

Management should monitor hand tools which can deteriorate with use, to ensure

they are sharpened or replaced as necessary and that the correct tools are being used

properly. Specific checks should be made as follows:

Chisels for mushroom heads

Hammer and file handles for deterioration and exposed tangs

Open-ended spanners for splayed jaws.

Operative should be instructed in the correct method of use and in maintenance

requirements at induction if not part of craft training.

General Office Building, Reception Refurbishment

Section 7, Page 12

SECTION SEVEN

Title: Introduction

Category: C.O.S.H.H. Instructions

Maintenance Instructions and Log Books

Item: 7.3.1

Page: 1 of 1

The Control of Substances Hazardous to Health (C.O.S.H.H.) 2002 regulation place a duty on employers

to ensure that their employees are not exposed tosubstanceshazardousto health, ie. to solids/liquids/gases

that are toxic/harmful/corrosive/irritant. Safety guidelines, for example, for concentrations of substances

in air, are separately prescribed by the appropriate authorities.

The following pages within this sub-section give a general indication of the potential hazards presented

and procedures for the safe storage, handling and disposal of the various chemicals and materials likely

to be encountered during the operation and maintenance of the system.

It  is  essential  however  that  the  specific  C.O.S.H.H.  data  sheet  (also  known  in  some  instances  as  a

Chemical Safety Data Sheet (C.S.D.S) or a Material Safety Data Sheet or M.S.D.S.) for any chemicals or

materials used are acquired, read, understood and followed by all personnel. The purpose therefore of this

sub-section is for planning information to ensure that all necessary procedures are in place prior to the

purchase of the chemicals or materials.

General Office Building, Reception Refurbishment

Section 7, Page 13

SECTION SEVEN

Title: Refrigerant Gas

Category: C.O.S.H.H. Instructions

Maintenance Instructions and Log Books

Item: 7.3.2

Page: 1 of 1

Description: This describes the general procedures for the safe storage, handling and disposal of

refrigerant gasses, together with how to treat contamination.

Health Hazard Data:

Skin Contact:

Eye Contact:

Inhalation:

Liquid splashes or sprays may cause freeze burns.

Liquid splashes or sprays may cause freeze burns.

Low toxicity with normal concentrations, high exposures can cause abnormal heart

rhythm and prove suddenly fatal. Very high exposures may cause anaesthetic

effects and asphyxiation.

Notes:

1. It is essential that the specific C.O.S.H.H. data sheet for the gas to be used is acquired, read,

understood and followed by all personnel prior to its use.

2. If there is any doubt as to the subjects condition then medical attention should be sought

immediately.

Procedure

Storage

Actions

The canisters should be stored in a cool (below

45 oC), dry, well ventilated space away from

sunlight and sources of heat. The canisters

should be stored away from ventilation intakes

of any system and away from open drains.

Notes

Handling

Use specialised refrigerant charging equipment

and suitable respiratory equipment in

unventilated spaces. Charging should be made

using the liquid phase and not the vapour phase.

Refrigerant transfers can cause a

build up of static electricity, all

apparatus should be earthed. In

the event of leakage it should be

noted that refrigerant gasses will

accumulate at floor level.

Disposal

Skin Contact

Unwanted refrigerant gas should be collected

for recycling if at all possible, or else destroyed

by a suitably licensed agent.

Thaw affected areas with warm water, remove

contaminated clothing.

Remove any contact lenses and wash eyes with

copious amounts of fresh water.

Relocate the subject to the fresh air and perform

artificial respiration if necessary.

Do not induce vomiting. If conscious drink

250ml of water and keep warm.

Eye Contact

Inhalation

Ingestion

Clothing may be frozen to skin,

thaw first.

Behind the eye lids should also

be washed for 15 minutes. Seek

medical attention immediately.

Seek medical attention

immediately.

Seek medical attention

immediately.

General Office Building, Reception Refurbishment

Section 7, Page 14

SECTION SEVEN

Title: Foam Insulation

Category: C.O.S.H.H. Instructions

Maintenance Instructions and Log Books

Item: 7.3.3

Page: 1 of 1

Description: This describes the general procedures for the safe storage, handling and disposal of

foam based insulating materials, together with how to treat contamination.

Health Hazard Data:

Skin Contact:

Eye Contact:

Inhalation:

Notes:

No observed hazards.

In particulate form irritation may occur.

Potential irreversible effects if burnt.

1. It is essential that the specific C.O.S.H.H. data sheet for the material to be used is acquired, read,

understood and followed by all personnel prior to its use.

2. If there is any doubt as to the subjects condition then medical attention should be sought

immediately.

Procedure

Storage

Handling

Disposal

Skin Contact

Eye Contact

Inhalation

Actions

There are no special storage requirements for

this product.

Gloves and goggles should be used when

installing.

General good housekeeping measures should

prove sufficient. Controlled combustion and

burial are required for large quantities.

Any contact with burning material should be

doused with cold water, but not removed.

Treat as any particulate such as dust or grit.

Not applicable unless burnt.

Notes

Seek medical attention

immediately.

Ingestion

Do not induce vomiting.

Seek medical attention

immediately.

Seek medical attention

immediately.

General Office Building, Reception Refurbishment

Section 7, Page 15

SECTION SEVEN

Title: General Maintenance Log Book

Category: Sample Log Books

System Description:

Date

Description of Action Taken

Maintenance Instructions and Log Books

Item: 7.4.1

Page: 1 of 1

Page Number:

By (Sign & Print)

General Office Building, Reception Refurbishment

Section 7, Page 16

SECTION EIGHT

FAULT TRACING CHARTS

SECTION EIGHT

INDEX

ITEM

8.1

8.1.1

8.1.2

-

-

-

Fault Tracing Charts

DESCRIPTION

GENERAL

Introduction

Preliminary Investigation

MISCELLANEOUS EQUIPMENT

Direct Expansion Air Conditioning Unit

Compressor

Fan

Small Fan

Coil (DX)

Motor

8.2

8.2.1

8.2.2

8.2.3

8.2.4

8.2.5

8.2.6

-

-

-

-

-

-

-

General Office Building, Reception Refurbishment

Section 8, Page 2

SECTION EIGHT

Title: Introduction

Category: General

Fault Tracing Charts

Item: 8.1.1

Page: 1 of 1

Fault tracing of the electrical installation or appliances that are connected to the installation should only

be carried out by suitably trained competent personnel.

Whenever possible all fault tracing should be carried out on circuits, appliances or components after they

have been suitably isolated from the main supply.

When it is not possible to carry out fault tracing on a "dead" installation, then the fault tracing must be

carried out by a minimum of two people.

Prior to carrying out any fault tracing it is essential that the personnel involved read the health and safety

section of this manual and familiarise themselves with the operation and maintenance sections.

General Office Building, Reception Refurbishment

Section 8, Page 3

SECTION EIGHT

Title: Preliminary Investigation

Category: General

Fault Tracing Charts

Item: 8.1.2

Page: 1 of 1

Following a reported failure of an appliance, the likely cause can be quickly established by asking the

relevant question of those in the vicinity of the failure.

a)

b)

c)

d)

e)

f)

g)

h)

Was the appliance or component operating when it failed, or did it fail to start?

Do other items of equipment on the same circuit still operate?

Has the correct operating procedure been carried out?

When was the last time the component/appliance was used?

Had there been any signs of deterioration in the performance or any increase in noise levels from

the appliance/component?

Has there been any maintenance work carried out prior to the failure?

Has any work been carried out in the vicinity of the failure, or along the route of the failed circuit

prior to the failure?

Has anyone else investigated the failure prior to those now required to do so and if so what did

they do and what did they find out?

General Office Building, Reception Refurbishment

Section 8, Page 4

SECTION EIGHT

Title: Direct Expansion Air Conditioning Unit - Indoor Unit

Category: Miscellaneous Equipment

Symptom              Possible Cause

Fault Tracing Charts

Item: 8.2.1

Page: 1 of 4

Electrical

Fan Not

Working

Drive Mechanism

Electrical

Resistance

Duty Low

Refrigerant

Duty High

Electrical

Resistance

Drive Mechanism

Excessive

Vibration

General

Checks

Check that electrical supply is available at fan.

Check local isolator is switched on.

Check for loose electrical connections.

Check controller is calling for fan to run.

Check motor is working.

Check if fan blowers are aligned.

Check inlet and outlet of fan for obstruction.

Check for correct supply voltage.

Check for correct control set points.

Check condition of air filter.

Check condition of evaporator fins for fouling.

Check for correct system balance.

Check for leaks in systems.

Check for excessive high head pressure.

Check for blocked expansion valve orifice.

Check for correct supply voltage.

Check for correct controls set points.

Check correct system balance.

Check for correct balance of fan impeller.

Check condition of bearings.

Check for drive shaft distortion.

Check motor balance.

Check security of casing.

Check security of pipework.

General Office Building, Reception Refurbishment

Section 8, Page 5

SECTION EIGHT

Title: Direct Expansion Air Conditioning Unit - Indoor Unit

Category: Miscellaneous Equipment

Symptom

Excessive

Vibration

(Continued)

Possible Cause

Fault Tracing Charts

Item: 8.2.1

Page: 2 of 4

Mountings

Excessive Noise

Water Leakage

Drive Mechanism

Damage

Vibration

Blocked Drain

Checks

Check security of mounting bolts.

Check condition of anti-vibration mounts.

Check condition of bearings.

Check condition of motor.

Check impeller for impingement on casing.

Refer to previous symptom.

Check condensate tray for obstruction.

Check condensate drain for obstruction.

General Office Building, Reception Refurbishment

Section 8, Page 6

SECTION EIGHT

Title: Direct Expansion Air Conditioning Unit - Outdoor Unit

Category: Miscellaneous Equipment

Symptom              Possible Cause

Fault Tracing Charts

Item: 8.2.1

Page: 3 of 4

Electrical

Fan Not

Operating

Drive Mechanism

Compressor Not

Operating

Electrical

Mechanical

Drive Mechanism

Excessive

Vibration

General

Mountings

Drive Mechanism

(Fan)

Excessive Noise

Compressor Fault

Checks

Check that electrical supply is available at fan.

Check that local isolator is switched on.

Check for loose electrical connections.

Check controller is calling for fan to run.

Check motor is working.

Check fan is free to rotate.

Check that electrical supply is available at compressor.

Check isolator is on.

Check for loose electrical connections.

Check for compressor motor failure.

Check for compressor seizure.

Check for correct balance of fan impeller.

Check condition of bearings.

Check motor balance.

Check security of casing.

Check security of pipework.

Check security of mounting bolts.

Check security of anti-vibration mounts.

Check condition of bearings.

Check condition of motor.

Check oil level.

Check for broken or damaged compressor valve reeds.

Check for worn or scored bearings.

General Office Building, Reception Refurbishment

Section 8, Page 7

SECTION EIGHT

Title: Direct Expansion Air Conditioning Unit - Outdoor Unit

Category: Miscellaneous Equipment

Symptom

Excessive Noise

Continued

Possible Cause

Damage

Vibration

Fan Not Working

Refrigerant

General

Fault Tracing Charts

Item: 8.2.1

Page: 4 of 4

Excessive Head

Pressure

Low Suction

Pressure

Refrigerant

General

Refrigerant

Controls

Compressor

Excessive

Suction

Pressure

Checks

Check fan impeller for impingement on casing.

Refer to previous symptom.

Refer to previous symptom.

Check for overcharge of gas.

Check for contaminants in refrigerant lines.

Check condenser coil for obstruction.

Check piping for leaks.

Check refrigerant charge.

Check for obstruction in flow control device.

Check for clogged filter drier.

Check for obstruction or icing on coil.

Check refrigerant charge.

Check flow through flow control device.

Check setting of head pressure controller.

Check for damage to compressor reeds.

General Office Building, Reception Refurbishment

Section 8, Page 8

SECTION EIGHT

Title: Compressor

Category: Miscellaneous Equipment

Symptom              Possible Cause

Fault Tracing Charts

Item: 8.2.2

Page: 1 of 1

Electrical

Will Not

Operate

Stops

Controls

Motor

Mechanical

Electrical

Controls

Pipeline

Compressor

Controls

Motor

Short Cycles

Pipeline

Controls

Runs

Continuously

Pipeline

Noisy

Compressor

Pipeline

Controls

Checks

Check if electrical supply is available at unit.

Check if local isolator is switched on.

Check for correct electrical supply voltage.

Check controls are calling for compressor to run.

Check for correct operation of all control components.

Check for a seized or burnt out motor.

Check for locked or damaged components.

Check for a loss of electrical supply.

Check for safety cut-out in controls.

Check refrigerant charge.

Check oil level.

Check for correct operation of controls.

Motor faulty.

Check condition of drier core.

Check condition of solenoid valves.

Check refrigerant charge.

Check for correct operation of controls.

Check refrigerant charge.

Check condition of drier core.

Check condition of solenoid valve.

Check oil level.

Check for broken internal components.

Check for correct operation of solenoid valves.

Check for correct operation of control items.

General Office Building, Reception Refurbishment

Section 8, Page 9

SECTION EIGHT

Title: Fan

Category: Miscellaneous Equipment

Symptom              Possible Cause

Fault Tracing Charts

Item: 8.2.3

Page: 1 of 1

Electrical Supply

Not Running

Drive Mechanism

Electrical Supply

Duty Low

Resistance

Duty High

Electrical Supply

Resistance

Drive Mechanism

Excessive

Vibration

Mountings

Excessive Noise

Drive Mechanism

Damage

Vibration

Checks

Check that electrical supply is available at fan.

Check local isolator is switched on.

Check controller is calling for fan to run.

Check motor is working.

Check for correct supply voltage.

Check for correct speed setting.

Check inlet and outlet of fan for obstruction.

Check for correct system balance.

Check for correct supply voltage.

Check for correct speed setting.

Check for correct system balance.

Check for correct balance of fan impeller.

Check condition of bearings.

Check for drive shaft distortion.

Check motor balance.

Check security of holding down bolts.

Check condition of anti-vibration mounts.

Check condition of bearings.

Check condition of motor.

Check impeller for impingement on casing.

Refer to previous symptom.

General Office Building, Reception Refurbishment

Section 8, Page 10

SECTION EIGHT

Title: Small Fan

Category: Miscellaneous Equipment

Symptom              Possible Cause

Fault Tracing Charts

Item: 8.2.4

Page: 1 of 1

Electrical Supply

Not Running

Duty Low

Duty High

Drive Mechanism

Electrical Supply

Drive Mechanism

Resistance

Electrical Supply

Excessive Noise

Drive Mechanism

Damage

Checks

Check that electrical supply is available at fan.

Check local isolator is switched on.

Check controller is calling for fan to run.

Check motor is working.

Check for correct supply voltage.

Check for correct speed setting.

Check impeller is secure on shaft.

Check inlet and outlet of fan for obstruction.

Check for correct supply voltage.

Check for correct speed setting.

Check impeller is secure on shaft.

Check condition of motor.

Check impeller for impingement on casing.

General Office Building, Reception Refurbishment

Section 8, Page 11

SECTION EIGHT

Title: Coil (DX)

Category: Miscellaneous Equipment

Symptom              Possible Cause

Excessive

Cooling

Controls

Refrigerant

Controls

Fault Tracing Charts

Item: 8.2.5

Page: 1 of 1

Insufficient

Cooling

Refrigerant

Checks

Check for correct operation of thermostats and sensors.

Check for correct response at controller.

Check for correct operating pressure.

Check for correct operation of thermostats and sensors.

Check for correct response at controller.

Check for leaks in systems.

Check for correct operating pressure.

General Office Building, Reception Refurbishment

Section 8, Page 12

SECTION EIGHT

Title: Motor

Category: Miscellaneous Equipment

Fault Tracing Charts

Item: 8.2.6

Page: 1 of 6

The most common cause of faults that occur is due to motors of pumps or fans. This chart has therefore

been structured differently from the rest so as to lead not only to the cause but also to the remedy.

Step

1

Type

Test

Probable

Fault

Test

Details

Are all isolators switched on.

Answer

Yes

No

-

Yes

No

Yes

No

Yes

No

-

-

Yes

No

-

Yes

No

-

-

Yes

No

-

Go To Step

4

2

3

END

4

5

8

7

6

3

6

13

9

10

12

11

END

8

14 & 15

23

3

2

3

Switch isolators on.

Does motor start to run.

4

Test

Are any fuses ruptured.

5

6

7

8

Test

Action

Probable

Fault

Test

Are there any short circuits between phase to

neutral or phase to earth.

Replace ruptured fuses.

Repair short circuits.

Are all phase voltages satisfactory.

Check all phase voltages back to incoming

supply.

Are all phase voltages satisfactory at incoming

supply.

Refer to local electricity board.

Correct unsatisfactory voltage checking for

loose connections, etc.

Is starter tripped on a thermal overload

condition.

Reset the overload current.

9

Test

10

11

12

13

14

Test

Action

Probable

Fault

Test

Action

General Office Building, Reception Refurbishment

Section 8, Page 13

SECTION EIGHT

Title: Motor

Category: Miscellaneous Equipment

Step

15

Type

Action

Fault Tracing Charts

Item: 8.2.6

Page: 2 of 6

16

Test

Details

Measure the output current and voltage from

starter.

Are the voltages equal.

17

Test

18

Test

19

Action

20

21

22

Probable

Fault

Action

Action

23

Test

Are overloads set correctly.

Is the current consumed:-

1) Fractionally higher than motor rating.

2) Excessively higher than motor rating.

Set overload unit slightly higher and allow

motor to run for 15 minutes.

Does motor run satisfactory without

overheating.

Check that motor is not excessively

overloaded. If so reduce the loading so the

motor is operating to its designed conditions.

Adjust overload unit to correct setting.

Trace exactly where the voltage drop occurs

and remedy by cleaning contacts.

Is the starter equipped with a thermistor

protector.

Answer

-

Yes

No

Yes

No

-

Yes

Yes

Yes

Go To Step

16

17

22

18

21

-

19

20

END

No

20

-

-

13

13

24

Test

Is the thermistor protection tripped.

25

Test

Probable

Fault

26

Is the wiring of the thermistor and the

resistance of the thermistor circuit satisfactory.

Motor mounted thermistor may be burnt out or

wiring may be broken.

-

Yes

No

Yes

No

Yes

No

-

13

24

28

25

28

27

26

END

General Office Building, Reception Refurbishment

Section 8, Page 14

SECTION EIGHT

Title: Motor

Category: Miscellaneous Equipment

Step

27

28

Type

Action

Test

Details

Reset thermistor protector unit.

Is the starter equipped with an earth leakage

protector circuit.

Fault Tracing Charts

Item: 8.2.6

Page: 3 of 6

29

Test

Is the earth leakage protector tripped.

30

Test

Probable

Fault

Action

Is the an earth leakage fault or any wiring fault

on the earth leakage circuit.

Earth Leakage.

Reset earth leakage protector unit.

Answer

-

Yes

No

Yes

No

Yes

No

-

-

D.O.L.

A.S.D.

Stator

Rotor

Auto-

Trans

Vapour-

matic

Yes

No

Yes

No

-

Go To Step

3

29

33

30

33

31

32

END

3

34

37

41

31

32

33

Test

What type of starter is used.

34

Test

Does the starter contactor operate.

35

Test

Probable

Fault

Is there any voltage across the contactor coil

terminals.

Contactor coil burnt out.

44

34

47

35

36

48

END

36

General Office Building, Reception Refurbishment

Section 8, Page 15

SECTION EIGHT

Title: Motor

Category: Miscellaneous Equipment

Step           Type

Fault Tracing Charts

Item: 8.2.6

Page: 4 of 6

37

Test

Details

Do the starter contactors operate:-

Main Contactor

Star Contactor

Delta Contactor

38

Test

39

Test

40

Probable

Fault

41

Test

Is there any voltage across the contactor coil

terminals.

Check timer unit for correct action

remembering when initially started the Star

and Main Contactors should be energised and

at the end of the time period the Delta and

Main Contactors should be energised.

Timer unit may be faulty or wiring associated

may be faulty

Do the starter contactors operate:-

Main Contactor

Subsidiary Contactors

Answer

Yes

No

Yes

No

Yes

No

Yes

No

Correct

Go To Step

39

35

39

38

39

38

36

39

49

Incorrect

40

42

Test

43

Test

Is there any voltage across the contactor coil.

Check timing circuits for correct action

remembering when initially started the Main

Contactor should be energised and at the end

of each time period a subsidiary contactor will

also be energised, until all are energised.

-

Yes

No

Yes

No

Yes

No

Correct

END

43

35

43

42

36

43

49

Incorrect

40

General Office Building, Reception Refurbishment

Section 8, Page 16

SECTION EIGHT

Title: Motor

Category: Miscellaneous Equipment

Step           Type

Fault Tracing Charts

Item: 8.2.6

Page: 5 of 6

44

Test

Details

Do the starter contactors operate:-

Main Contactor

Subsidiary Contactors

45

Test

46

Test

47

Test

Probable

Fault

Test

Is there any voltage across the contactor coil

terminals.

Check timing circuits for correct action

remembering when initially started the Star

and Load Contactors should be energised and

at the end of the time period the Run Contactor

should be energised whilst the Star and Load

Contactors should be de-energised.

Check the control action of the starter.

Control circuit wiring of the started may be

faulty.

Are the motor windings open circuit.

Answer

Yes

No

Yes

No

Yes

No

Correct

Go To Step

46

35

46

45

36

46

49

Incorrect

Correct

Incorrect

-

Yes

No

Yes

No

Yes

No

Satis-

factory

Not Satis-

factory

40

49

48

END

53

50

51

53

52

53

56

48

49

50

Test

Are the motor windings of equal resistance.

51

Test

Is there continuity through all the contactors

when contacts are closed.

52

Test

53

Probable

Fault

Is the wiring between the starter and the motor

satisfactory, i.e. are there any breakages or

high resistances.

Any one of the motor windings being open

circuit or of different resistance would result in

an unbalance load.

55

-

END

General Office Building, Reception Refurbishment

Section 8, Page 17

SECTION EIGHT

Title: Motor

Category: Miscellaneous Equipment

Step

54

Fault Tracing Charts

Item: 8.2.6

Page: 6 of 6

55

56

Type

Probable

Fault

Probable

Fault

-

Details

Discontinuity through contacts would not

allow the motor to run.

Broken wiring or high resistance wiring would

result in an unbalance load.

Problem not found - Go back to Step 1.

Answer

-

Go To Step

END

-

-

END

1

General Office Building, Reception Refurbishment

Section 8, Page 18

SECTION NINE

MANUFACTURERS' LITERATURE

SECTION NINE

INDEX

ITEM

9.1

9.1.1

9.1.2

-

-

-

Manufacturers' Literature

DESCRIPTION

MANUFACTURERS' LITERATURE

Mitsubishi Electric Europe Ltd   PEAD-RP Internal Air Conditioning Unit

Mitsubishi Electric Europe Ltd   PUHZ-RP External Air Conditioning Unit

General Office Building, Reception Refurbishment

Section 9, Page 2

SECTION TEN

TEST CERTIFICATES AND COMMISSIONING DATA

SECTION TEN

INDEX

ITEM

10.1

10.1.1

10.1.2

10.1.3

-

-

-

-

Test Certificates and Commissioning Data

DESCRIPTION

HEATING AND COOLING SYSTEMS

Refrigeration Pipework Pressure Test Certificate

Air Conditioning System Commissioning Report

Condensate Pipework Flood Discharge Test Certificate

General Office Building, Reception Refurbishment

Section 10, Page 2

SECTION ELEVEN

SPECIALIST SERVICES DOCUMENTATION

SECTION ELEVEN

CONTENTS

ITEM

11.1

11.1.1

-

-

Specialist Services Documentation

DESCRIPTION

SPECIALIST SERVICES DOCUMENTATION

A N Other Controls Company Ltd           Mechanical Services Control System

General Office Building, Reception Refurbishment

Section 11, Page 2

SECTION TWELVE

RECORD DRAWINGS

SECTION TWELVE

INDEX

ITEM

12.1

12.1.1

-

-

Record Drawings

DESCRIPTION

RECORD DRAWINGS

Schedule of Record Drawings

General Office Building, Reception Refurbishment

Section 12, Page 2

SECTION TWELVE

Title: Schedule of Record Drawings

Category: Record Drawings

Number

RD01

RD02

Size

A1

A1

Record Drawings

Item: 12.1.1

Page: 1 of 1

Title

Ground Floor Reception Mechanical Services Layout

Roof Level Mechanical Services Layout

General Office Building, Reception Refurbishment

Section 12, Page 3